## Contamination in DUWLs
Sampling site | Sample-ID | Sampling points | Sampling time | Post/Pre-Operation | Downtime | Compliance state (＜500CFU/ml) | Heterotrophic plate counts
Water source | 0-0 | Water purification system outlet | / | / | / | 0 | 0
Water source | 0-1 | storage tank effluent | / | / | / | 0 | 0
Main distribution piping | 0-2 | Main supply inlet (pre-filtration) | / | / | / | 0 | 0
Main distribution piping | 0-3 | Main supply inlet (pre-filtration) | / | / | / | 0 | 0
Main distribution piping | 0-4 | Point-of-entry (POE, post-filtration) | / | / | / | 0 | 0
Main distribution piping | 0-5 | Manifold junction (pre-branching) | / | / | / | 0 | 0
Main distribution piping | 0-6 | Manifold junction (pre-branching) | / | / | / | 0 | 0
V1 | V1-1 | High-speed handpiece outlet | Morning Sampling | 0 | 1 | 1 | >500
V1 | V1-2 | Air-water syringe outlet | Morning Sampling | 0 | 1 | 1 | >500
V1 | V1-3 | Cup filler outlet | Morning Sampling | 0 | 1 | 1 | >500
V1 | V1-4 | Ultrasonic scaler outlet | Morning Sampling | 0 | 1 | 1 | >500
V2 | V2-1 | High-speed handpiece outlet | Morning Sampling | 1 | 1 | 1 | >500
V2 | V2-2 | Air-water syringe outlet | Morning Sampling | 1 | 1 | 1 | >500
V2 | V2-3 | Cup filler outlet | Morning Sampling | 1 | 1 | 1 | >500
V2 | V2-4 | Ultrasonic scaler outlet | Morning Sampling | 1 | 1 | 1 | >500
V3 | V3-1 | High-speed handpiece outlet | Morning Sampling | 0 | 1 | 1 | >500
V3 | V3-2 | Air-water syringe outlet | Morning Sampling | 0 | 1 | 1 | >500
V3 | V3-3 | Cup filler outlet | Morning Sampling | 0 | 1 | 1 | >500
V3 | V3-4 | Ultrasonic scaler outlet | Morning Sampling | 0 | 1 | 1 | >500
Room 1 | 1-1 | High-speed handpiece outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 1 | 1-2 | Air-water syringe outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 1 | 1-3 | Cup filler outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 1 | 1-4 | Ultrasonic scaler outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 2 | 2-1 | High-speed handpiece outlet | Morning Sampling | 1 | 0 | 1 | >500
Room 2 | 2-2 | Air-water syringe outlet | Morning Sampling | 1 | 0 | 1 | >500
Room 2 | 2-3 | Cup filler outlet | Morning Sampling | 1 | 0 | 1 | >500
Room 2 | 2-4 | Ultrasonic scaler outlet | Morning Sampling | 1 | 0 | 1 | >500
Room 3 | 3-1 | High-speed handpiece outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 3 | 3-2 | Air-water syringe outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 3 | 3-3 | Cup filler outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 3 | 3-4 | Ultrasonic scaler outlet | Afternoon Sampling | 1 | 0 | 0 | 7
Room 4 | 4-1 | High-speed handpiece outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 4 | 4-2 | Air-water syringe outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 4 | 4-3 | Cup filler outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 4 | 4-4 | Ultrasonic scaler outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 5 | 5-1 | High-speed handpiece outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 5 | 5-2 | Air-water syringe outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 5 | 5-3 | Cup filler outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 5 | 5-4 | Ultrasonic scaler outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 6 | 6-1 | High-speed handpiece outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 6 | 6-2 | Air-water syringe outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 6 | 6-3 | Cup filler outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 6 | 6-4 | Ultrasonic scaler outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 7 | 7-1 | High-speed handpiece outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 7 | 7-2 | Air-water syringe outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 7 | 7-3 | Cup filler outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 7 | 7-4 | Ultrasonic scaler outlet | Afternoon Sampling | 1 | 0 | 1 | >500
Room 8 | 8-1 | High-speed handpiece outlet | Morning Sampling | 1 | 0 | 1 | >500
Room 8 | 8-2 | Air-water syringe outlet | Morning Sampling | 1 | 0 | 1 | >500
Room 8 | 8-3 | Cup filler outlet | Morning Sampling | 1 | 0 | 1 | >500
Room 8 | 8-4 | Ultrasonic scaler outlet | Morning Sampling | 1 | 0 | 1 | >500
Room 9 | 9-1 | High-speed handpiece outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 9 | 9-2 | Air-water syringe outlet | Morning Sampling | 0 | 0 | 0 | 0
Room 9 | 9-3 | Cup filler outlet | Morning Sampling | 0 | 0 | 0 | 0
Room 9 | 9-4 | Ultrasonic scaler outlet | Morning Sampling | 0 | 0 | 0 | 50
Room 10 | 10-1 | High-speed handpiece outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 10 | 10-2 | Air-water syringe outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 10 | 10-3 | Cup filler outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 10 | 10-4 | Ultrasonic scaler outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 11 | 11-1 | High-speed handpiece outlet | Morning Sampling | 0 | 0 | 1 | >500
Room 11 | 11-2 | Air-water syringe outlet | Morning Sampling | 0 | 0 | 0 | 4
Room 11 | 11-3 | Cup filler outlet | Morning Sampling | 0 | 0 | 0 | 1
Room 11 | 11-4 | Ultrasonic scaler outlet | Morning Sampling | 0 | 0 | 1 | >500
种植牙手术室 | 种植牙手术室-1 | High-speed handpiece outlet | Afternoon Sampling | 1 | 0 | 1 | >500
种植牙手术室 | 种植牙手术室-2 | Air-water syringe outlet | Afternoon Sampling | 1 | 0 | 1 | >500
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Afternoon Sampling | 1 | 0 | 1 | >500
种植牙手术室 | 种植牙手术室-4 | Ultrasonic scaler outlet | Afternoon Sampling | 1 | 0 | 1 | >500

## Protocol A
Sampling site | ID | Sampling points | Sampling time | Downtime | Post/Pre-Operation | Compliance state (＜500CFU/ml) | Heterotrophic plate counts | Time to Disinfection Initiation (TDI,Week)
Water source | 0-0 | Water purification system outlet | / | / | / | Compliance | 0 | /
Water source | 0-1 | storage tank effluent | / | / | / | Compliance | 0 | /
Room 10 | 10-1-0 | high-speed handpiece | Afternoon Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 10 | 10-2-0 | air/water syringes | Afternoon Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 10 | 10-3-0 | Cup filler outlet | Afternoon Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 10 | 10-4-0 | ultrasonic scalers | Afternoon Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 4 | 4-1-1 | high-speed handpiece | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room 4 | 4-2-1 | air/water syringes | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room 4 | 4-3-1 | Cup filler outlet | Afternoon Sampling | 24-48h | 1 | Compliance | 1 | 1
Room 4 | 4-4-1 | ultrasonic scalers | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room 10 | 10-1-1 | high-speed handpiece | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room 10 | 10-2-1 | air/water syringes | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room 10 | 10-3-1 | Cup filler outlet | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room 10 | 10-4-1 | ultrasonic scalers | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room V1 | V1-1-1 | high-speed handpiece | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room V1 | V1-2-1 | air/water syringes | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room V1 | V1-3-1 | Cup filler outlet | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room V1 | V1-4-1 | ultrasonic scalers | Afternoon Sampling | 24-48h | 1 | Compliance | 0 | 1
Room 4 | 4-1-2 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 4 | 4-2-2 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 4 | 4-3-2 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 4 | 4-4-2 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 10 | 10-1-2 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 10 | 10-2-2 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 10 | 10-3-2 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 10 | 10-4-2 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 4 | 4-1-3 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 4 | 4-2-3 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 11 | 1
Room 4 | 4-3-3 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 4 | 4-4-3 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 10 | 10-1-3 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 450 | 1
Room 10 | 10-2-3 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 10 | 10-3-3 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 4 | 1
Room 10 | 10-4-3 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 0 | 1
Room 4 | 4-1-5 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 12 | 1
Room 4 | 4-2-5 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 42 | 1
Room 4 | 4-3-5 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 40 | 1
Room 4 | 4-4-5 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 50 | 1
Room 10 | 10-1-5 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 10 | 10-2-5 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 10 | 10-3-5 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 10 | 10-4-5 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 0 | 1
Room 4 | 4-1-8 | high-speed handpiece | Morning Sampling | 24-48h | 0 | Compliance | 400 | 2
Room 4 | 4-2-8 | air/water syringes | Morning Sampling | 24-48h | 0 | Compliance | 30 | 2
Room 4 | 4-3-8 | Cup filler outlet | Morning Sampling | 24-48h | 0 | Compliance | 80 | 2
Room 4 | 4-4-8 | ultrasonic scalers | Morning Sampling | 24-48h | 0 | Compliance | 400 | 2
Room 10 | 10-1-8 | high-speed handpiece | Morning Sampling | 24-48h | 0 | Compliance | 320 | 2
Room 10 | 10-2-8 | air/water syringes | Morning Sampling | 24-48h | 0 | Compliance | 400 | 2
Room 10 | 10-3-8 | Cup filler outlet | Morning Sampling | 24-48h | 0 | Compliance | 400 | 2
Room 10 | 10-4-8 | ultrasonic scalers | Morning Sampling | 24-48h | 0 | Compliance | 400 | 2
Room 3 | 3-1-8 | high-speed handpiece | Morning Sampling | 24-48h | 0 | Compliance | 0 | 2
Room 3 | 3-2-8 | air/water syringes | Morning Sampling | 24-48h | 0 | Compliance | 0 | 2
Room 3 | 3-3-8 | Cup filler outlet | Morning Sampling | 24-48h | 0 | Compliance | 0 | 2
Room 3 | 3-4-8 | ultrasonic scalers | Morning Sampling | 24-48h | 0 | Compliance | 0 | 2
Room 6 | 6-1-8 | high-speed handpiece | Morning Sampling | 24-48h | 0 | Compliance | 124 | 2
Room 6 | 6-2-8 | air/water syringes | Morning Sampling | 24-48h | 0 | Compliance | 96 | 2
Room 6 | 6-3-8 | Cup filler outlet | Morning Sampling | 24-48h | 0 | Compliance | 168 | 2
Room 6 | 6-4-8 | ultrasonic scalers | Morning Sampling | 24-48h | 0 | Non-compliance | >500 | 2
Room V1 | V1-1-8 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Compliance | 8 | 2
Room V1 | V1-2-8 | air/water syringes | Morning Sampling | 48-72 | 0 | Compliance | 400 | 2
Room V1 | V1-3-8 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 250 | 2
Room V1 | V1-4-8 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Compliance | 0 | 2
Room V2 | V2-1-8 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Compliance | 0 | 2
Room V2 | V2-2-8 | air/water syringes | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 2
Room V2 | V2-3-8 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 90 | 2
Room V2 | V2-4-8 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Compliance | 68 | 2
Room V3 | V3-1-8 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Compliance | 7 | 2
Room V3 | V3-2-8 | air/water syringes | Morning Sampling | 48-72 | 0 | Compliance | 110 | 2
Room V3 | V3-3-8 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 3 | 2
Room V3 | V3-4-8 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Compliance | 4 | 2
Room 7 | 7-1-8 | high-speed handpiece | Morning Sampling | 24-48h | 0 | Compliance | 15 | 2
Room 7 | 7-4-8 | ultrasonic scalers | Morning Sampling | 24-48h | 0 | Compliance | 60 | 2
Room 11 | 11-1-8 | high-speed handpiece | Morning Sampling | 24-48h | 0 | Compliance | 10 | 2
Room 11 | 11-4-8 | ultrasonic scalers | Morning Sampling | 24-48h | 0 | Compliance | 40 | 2
手术室 | 手术室-1-8 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Compliance | 142 | 2
手术室 | 手术室-2-8 | air/water syringes | Morning Sampling | 48-72 | 0 | Compliance | 31 | 2
手术室 | 手术室-3-8 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 6 | 2
手术室 | 手术室-4-8 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Compliance | 28 | 2
Room 4 | 4-1-10 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 142 | 2
Room 4 | 4-2-10 | air/water syringes | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 2
Room 4 | 4-3-10 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 2
Room 4 | 4-4-10 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 2
Room 10 | 10-1-10 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 30 | 2
Room 10 | 10-2-10 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 76 | 2
Room 10 | 10-3-10 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 90 | 2
Room 10 | 10-4-10 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 14 | 2
Room 3 | 3-1-14 | high-speed handpiece | Morning Sampling | 72-96 | 1 | Non-compliance | >500 | 3
Room 3 | 3-2-14 | air/water syringes | Morning Sampling | 72-96 | 1 | Non-compliance | >500 | 3
Room 3 | 3-3-14 | Cup filler outlet | Morning Sampling | 72-96 | 1 | Non-compliance | >500 | 3
Room 3 | 3-4-14 | ultrasonic scalers | Morning Sampling | 72-96 | 1 | Non-compliance | >500 | 3
Room 7 | 7-1-14 | high-speed handpiece | Morning Sampling | 48-72 | 1 | Compliance | 400 | 3
Room 7 | 7-4-14 | ultrasonic scalers | Morning Sampling | 48-72 | 1 | Compliance | 320 | 3
Room 4 | 4-1-19 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 96 | 3
Room 4 | 4-2-19 | air/water syringes | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room 4 | 4-3-19 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room 4 | 4-4-19 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room V3 | V3-1-19 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 12 | 3
Room V3 | V3-2-19 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 9.4 | 3
Room V3 | V3-3-19 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 11 | 3
Room V3 | V3-4-19 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 0.4 | 3
Room V2 | V2-1-19 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room V2 | V2-2-19 | air/water syringes | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room V2 | V2-3-19 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 3 | 3
Room V2 | V2-4-19 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room 6 | 6-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 48 | 4
Room 6 | 6-1-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 32.8 | 4
Room 6 | 6-1-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 2.8 | 4
Room 6 | 6-1-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 50 | 4
Room 10 | 10-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 60 | 4
Room 10 | 10-1-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 5 | 4
Room 10 | 10-1-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 60 | 4
Room 10 | 10-1-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 32 | 4
Room 1 | 1-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 50 | 4
Room 1 | 1-2-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 50 | 4
Room 1 | 1-3-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 1.7 | 4
Room 1 | 1-4-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 100 | 4
Room 4 | 4-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 4
Room 4 | 4-1-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 4
Room 4 | 4-1-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 4
Room 4 | 4-1-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 4
Room 2 | 2-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 4
Room 2 | 2-1-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 4
Room 2 | 2-1-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 25 | 4
Room 2 | 2-1-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 4
手术室 | 手术室-1-26 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 4
手术室 | 手术室-2-26 | air/water syringes | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 4
手术室 | 手术室-3-26 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 4
手术室 | 手术室-4-26 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 4
Room V1 | V1-1-26 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 4
Room V1 | V1-2-26 | air/water syringes | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 4
Room V1 | V1-3-26 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 0.7 | 4
Room V1 | V1-4-26 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 4
Room 7 | 7-1-26 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 4
Room 7 | 7-2-26 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 40 | 4
Room 7 | 7-3-26 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 8 | 4
Room 7 | 7-4-26 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 40 | 4
Room 8 | 8-1-26 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 0.5 | 4
Room 8 | 8-1-26 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 1 | 4
Room 8 | 8-1-26 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 0.1 | 4
Room 8 | 8-1-26 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 2 | 4
Room V2 | V2-1-26 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 4
Room V2 | V2-2-26 | air/water syringes | Morning Sampling | 48-72 | 0 | Compliance | 30 | 4
Room V2 | V2-3-26 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 4
Room V2 | V2-4-26 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 4
手术室 | 手术室-1-38 | high-speed handpiece | Morning Sampling | 24-48h | 0 | Non-compliance | >500 | 5
手术室 | 手术室-2-38 | air/water syringes | Morning Sampling | 24-48h | 0 | Non-compliance | >500 | 5
手术室 | 手术室-3-38 | Cup filler outlet | Morning Sampling | 24-48h | 0 | Compliance | 55 | 5
手术室 | 手术室-4-38 | ultrasonic scalers | Morning Sampling | 24-48h | 0 | Non-compliance | >500 | 5
Room 8 | 8-1-38 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 80 | 5
Room 8 | 8-2-38 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 11 | 5
Room 8 | 8-3-38 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 12 | 5
Room 8 | 8-4-38 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 15 | 5
Room V2 | V2-1-38 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room V2 | V2-2-38 | air/water syringes | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room V2 | V2-3-38 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 50 | 5
Room V2 | V2-4-38 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room V1 | V1-1-38 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room V1 | V1-2-38 | air/water syringes | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room V1 | V1-3-38 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 16 | 5
Room V1 | V1-4-38 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room 10 | 10-1-38 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 10 | 10-2-38 | air/water syringes | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 10 | 10-3-38 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 10 | 10-4-38 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 3 | 3-1-38 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 3 | 3-2-38 | air/water syringes | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 3 | 3-3-38 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 3 | 3-4-38 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 1 | 1-1-38 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 45 | 5
Room 1 | 1-2-38 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 80 | 5
Room 1 | 1-3-38 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 25 | 5
Room 1 | 1-4-38 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 90 | 5
Room 2 | 2-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 2 | 2-2-23 | air/water syringes | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 2 | 2-3-23 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 2 | 2-4-23 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 6 | 6-1-23 | high-speed handpiece | Morning Sampling | 24-48h | 0 | Non-compliance | >500 | 5
Room 6 | 6-2-23 | air/water syringes | Morning Sampling | 24-48h | 0 | Non-compliance | >500 | 5
Room 6 | 6-3-23 | Cup filler outlet | Morning Sampling | 24-48h | 0 | Non-compliance | >500 | 5
Room 6 | 6-4-23 | ultrasonic scalers | Morning Sampling | 24-48h | 0 | Non-compliance | >500 | 5
Room 7 | 7-1-26 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 7 | 7-2-26 | air/water syringes | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 7 | 7-3-26 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room 7 | 7-4-26 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 5
Room V3 | V3-1-19 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room V3 | V3-2-19 | air/water syringes | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room V3 | V3-3-19 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 50 | 5
Room V3 | V3-4-19 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 5
Room 6 | 6-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 48 | 3
Room 6 | 6-1-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 32.8 | 3
Room 6 | 6-1-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 2.8 | 3
Room 6 | 6-1-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 50 | 3
Room 10 | 10-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 60 | 3
Room 10 | 10-1-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 5 | 3
Room 10 | 10-1-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 60 | 3
Room 10 | 10-1-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 32 | 3
Room 1 | 1-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Compliance | 50 | 3
Room 1 | 1-2-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Compliance | 50 | 3
Room 1 | 1-3-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 1.7 | 3
Room 1 | 1-4-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Compliance | 100 | 3
Room 2 | 2-1-23 | high-speed handpiece | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room 2 | 2-1-23 | air/water syringes | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room 2 | 2-1-23 | Cup filler outlet | Morning Sampling | ＜24 | 0 | Compliance | 25 | 3
Room 2 | 2-1-23 | ultrasonic scalers | Morning Sampling | ＜24 | 0 | Non-compliance | >500 | 3
Room V1 | V1-1-26 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 3
Room V1 | V1-2-26 | air/water syringes | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 3
Room V1 | V1-3-26 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Compliance | 0.7 | 3
Room V1 | V1-4-26 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 3
Room 7 | 7-1-26 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Non-compliance | >500 | 3
Room 7 | 7-2-26 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 40 | 3
Room 7 | 7-3-26 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 8 | 3
Room 7 | 7-4-26 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 40 | 3
Room 8 | 8-1-26 | high-speed handpiece | Morning Sampling | ＜24 | 1 | Compliance | 0.5 | 3
Room 8 | 8-1-26 | air/water syringes | Morning Sampling | ＜24 | 1 | Compliance | 1 | 3
Room 8 | 8-1-26 | Cup filler outlet | Morning Sampling | ＜24 | 1 | Compliance | 0.1 | 3
Room 8 | 8-1-26 | ultrasonic scalers | Morning Sampling | ＜24 | 1 | Compliance | 2 | 3
Room V2 | V2-1-26 | high-speed handpiece | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 3
Room V2 | V2-2-26 | air/water syringes | Morning Sampling | 48-72 | 0 | Compliance | 30 | 3
Room V2 | V2-3-26 | Cup filler outlet | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 3
Room V2 | V2-4-26 | ultrasonic scalers | Morning Sampling | 48-72 | 0 | Non-compliance | >500 | 3

## Protocol B
Sampling site | ID | Sampling points | Compliance state (＜500CFU/ml) | Heterotrophic plate counts | Time to Disinfection Initiation (TDI,Week)
Water source | 0-0 | Water purification system outlet | Compliance | 0 | /
Water source | 0-1 | storage tank effluent | Compliance | 0 | /
V1 | V1-1 | high-speed handpiece | Non-compliance | 600 | 1
V1 | V1-2 | air/water syringes | Compliance | 0 | 1
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 1
V1 | V1-4 | ultrasonic scalers | Compliance | 20 | 1
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 1
V2 | V2-2 | air/water syringes | Compliance | 0 | 1
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 1
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 1
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 1
V3 | V3-2 | air/water syringes | Compliance | 0 | 1
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 1
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 1
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 1
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 1
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 1
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 1
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 1
Room 2 | 2-2 | air/water syringes | Non-compliance | 500 | 1
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 1
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 1
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 1
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 1
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 1
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 1
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 1
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 1
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 1
Room 4 | 4-4 | ultrasonic scalers | Compliance | 30 | 1
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 1
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 1
Room 5 | 5-3 | Cup filler outlet | Compliance | 10 | 1
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 1
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 1
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 1
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 1
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 1
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 1
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 1
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 1
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 1
Room 8 | 8-1 | high-speed handpiece | Compliance | 3 | 1
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 1
Room 8 | 8-3 | Cup filler outlet | Compliance | 400 | 1
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 1
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 1
Room 9 | 9-2 | air/water syringes | Compliance | 56 | 1
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 1
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 1
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 1
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 1
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 1
Room 10 | 10-4 | ultrasonic scalers | Compliance | 6 | 1
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 1
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 1
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 1
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 1
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 5 | 1
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 1
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 1
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 3 | 1
V1 | V1-1 | high-speed handpiece | Compliance | 3 | 2
V1 | V1-2 | air/water syringes | Compliance | 0 | 2
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 2
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 2
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 2
V2 | V2-2 | air/water syringes | Compliance | 0 | 2
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 2
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 2
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 2
V3 | V3-2 | air/water syringes | Compliance | 5 | 2
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 2
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 2
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 2
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 2
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 2
Room 1 | 1-4 | ultrasonic scalers | Compliance | 8 | 2
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 2
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 2
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 2
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 2
Room 3 | 3-1 | high-speed handpiece | Compliance | 3 | 2
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 2
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 2
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 2
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 2
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 2
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 2
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 2
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 2
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 2
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 2
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 2
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 2
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 2
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 2
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 2
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 2
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 2
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 2
Room 7 | 7-4 | ultrasonic scalers | Compliance | 5 | 2
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 2
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 2
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 2
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 2
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 2
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 2
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 2
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 2
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 2
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 2
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 2
Room 10 | 10-4 | ultrasonic scalers | Compliance | 7 | 2
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 2
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 2
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 2
Room 11 | 11-4 | ultrasonic scalers | Compliance | 10 | 2
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 2
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 2
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 2
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 2
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 3
V1 | V1-2 | air/water syringes | Compliance | 0 | 3
V1 | V1-3 | Cup filler outlet | Compliance | 5 | 3
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 3
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 3
V2 | V2-2 | air/water syringes | Compliance | 0 | 3
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 3
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 3
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 3
V3 | V3-2 | air/water syringes | Compliance | 0 | 3
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 3
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 3
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 3
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 3
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 3
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 3
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 3
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 3
Room 2 | 2-3 | Cup filler outlet | Compliance | 6 | 3
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 3
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 3
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 3
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 3
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 3
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 3
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 3
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 3
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 3
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 3
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 3
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 3
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 3
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 3
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 3
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 3
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 3
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 3
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 3
Room 7 | 7-3 | Cup filler outlet | Compliance | 5 | 3
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 3
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 3
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 3
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 3
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 3
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 3
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 3
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 3
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 3
Room 10 | 10-1 | high-speed handpiece | Compliance | 5 | 3
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 3
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 3
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 3
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 3
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 3
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 3
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 3
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 9 | 3
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 3
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 3
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 3
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 4
V1 | V1-2 | air/water syringes | Compliance | 0 | 4
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 4
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 4
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 4
V2 | V2-2 | air/water syringes | Compliance | 0 | 4
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 4
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 4
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 4
V3 | V3-2 | air/water syringes | Compliance | 0 | 4
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 4
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 4
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 4
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 4
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 4
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 4
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 4
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 4
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 4
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 4
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 4
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 4
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 4
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 4
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 4
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 4
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 4
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 4
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 4
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 4
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 4
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 4
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 4
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 4
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 4
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 4
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 4
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 4
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 4
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 4
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 4
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 4
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 4
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 4
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 4
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 4
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 4
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 4
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 4
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 4
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 4
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 4
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 4
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 4
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 4
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 4
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 4
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 4
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 4
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 4
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 5
V1 | V1-2 | air/water syringes | Compliance | 0 | 5
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 5
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 5
V2 | V2-1 | high-speed handpiece | Compliance | 10 | 5
V2 | V2-2 | air/water syringes | Compliance | 0 | 5
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 5
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 5
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 5
V3 | V3-2 | air/water syringes | Compliance | 0 | 5
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 5
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 5
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 5
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 5
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 5
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 5
Room 2 | 2-1 | high-speed handpiece | Compliance | 6 | 5
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 5
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 5
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 5
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 5
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 5
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 5
Room 3 | 3-4 | ultrasonic scalers | Compliance | 3 | 5
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 5
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 5
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 5
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 5
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 5
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 5
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 5
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 5
Room 6 | 6-1 | high-speed handpiece | Compliance | 5 | 5
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 5
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 5
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 5
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 5
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 5
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 5
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 5
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 5
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 5
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 5
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 5
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 5
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 5
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 5
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 5
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 5
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 5
Room 10 | 10-3 | Cup filler outlet | Compliance | 10 | 5
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 5
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 5
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 5
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 5
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 5
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 5
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 6 | 5
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 5
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 5
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 6
V1 | V1-2 | air/water syringes | Compliance | 0 | 6
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 6
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 6
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 6
V2 | V2-2 | air/water syringes | Compliance | 0 | 6
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 6
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 6
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 6
V3 | V3-2 | air/water syringes | Compliance | 0 | 6
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 6
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 6
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 6
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 6
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 6
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 6
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 6
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 6
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 6
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 6
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 6
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 6
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 6
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 6
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 6
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 6
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 6
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 6
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 6
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 6
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 6
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 6
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 6
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 6
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 6
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 6
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 6
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 6
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 6
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 6
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 6
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 6
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 6
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 6
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 6
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 6
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 6
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 6
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 6
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 6
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 6
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 6
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 6
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 6
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 6
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 6
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 6
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 6
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 6
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 6
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 7
V1 | V1-2 | air/water syringes | Compliance | 0 | 7
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 7
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 7
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 7
V2 | V2-2 | air/water syringes | Compliance | 0 | 7
V2 | V2-3 | Cup filler outlet | Compliance | 400 | 7
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 7
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 7
V3 | V3-2 | air/water syringes | Compliance | 0 | 7
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 7
V3 | V3-4 | ultrasonic scalers | Compliance | 14 | 7
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 7
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 7
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 7
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 7
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 7
Room 2 | 2-2 | air/water syringes | Compliance | 6 | 7
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 7
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 7
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 7
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 7
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 7
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 7
Room 4 | 4-1 | high-speed handpiece | Compliance | 3 | 7
Room 4 | 4-2 | air/water syringes | Compliance | 20 | 7
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 7
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 7
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 7
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 7
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 7
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 7
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 7
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 7
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 7
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 7
Room 7 | 7-1 | high-speed handpiece | Compliance | 20 | 7
Room 7 | 7-2 | air/water syringes | Compliance | 10 | 7
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 7
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 7
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 7
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 7
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 7
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 7
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 7
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 7
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 7
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 7
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 7
Room 10 | 10-2 | air/water syringes | Compliance | 25 | 7
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 7
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 7
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 7
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 7
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 7
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 7
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 7
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 32 | 7
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 30 | 7
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 7
V1 | V1-1 | high-speed handpiece | Non-compliance | 12 | 11
V1 | V1-2 | air/water syringes | Compliance | 0 | 11
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 11
V1 | V1-4 | ultrasonic scalers | Compliance | 5 | 11
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 11
V2 | V2-2 | air/water syringes | Compliance | 10 | 11
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 11
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 11
V3 | V3-1 | high-speed handpiece | Compliance | 550 | 11
V3 | V3-2 | air/water syringes | Compliance | 0 | 11
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 11
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 11
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 11
Room 1 | 1-2 | air/water syringes | Compliance | 10 | 11
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 11
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 11
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 11
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 11
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 11
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 11
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 11
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 11
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 11
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 11
Room 4 | 4-1 | high-speed handpiece | Compliance | 7 | 11
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 11
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 11
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 11
Room 5 | 5-1 | high-speed handpiece | Compliance | 6 | 11
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 11
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 11
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 11
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 11
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 11
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 11
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 11
Room 7 | 7-1 | high-speed handpiece | Compliance | 8 | 11
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 11
Room 7 | 7-3 | Cup filler outlet | Compliance | 5 | 11
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 11
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 11
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 11
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 11
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 11
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 11
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 11
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 11
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 11
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 11
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 11
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 11
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 11
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 11
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 11
Room 11 | 11-3 | Cup filler outlet | Compliance | 10 | 11
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 11
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 11
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 11
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 11
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 11
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 15
V1 | V1-2 | air/water syringes | Compliance | 0 | 15
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 15
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 15
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 15
V2 | V2-2 | air/water syringes | Compliance | 0 | 15
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 15
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 15
V3 | V3-1 | high-speed handpiece | Compliance | 7 | 15
V3 | V3-2 | air/water syringes | Compliance | 0 | 15
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 15
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 15
Room 1 | 1-1 | high-speed handpiece | Compliance | 9 | 15
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 15
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 15
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 15
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 15
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 15
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 15
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 15
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 15
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 15
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 15
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 15
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 15
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 15
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 15
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 15
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 15
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 15
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 15
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 15
Room 6 | 6-1 | high-speed handpiece | Compliance | 10 | 15
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 15
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 15
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 15
Room 7 | 7-1 | high-speed handpiece | Compliance | 5 | 15
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 15
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 15
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 15
Room 8 | 8-1 | high-speed handpiece | Compliance | 6 | 15
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 15
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 15
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 15
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 15
Room 9 | 9-2 | air/water syringes | Compliance | 3 | 15
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 15
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 15
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 15
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 15
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 15
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 15
Room 11 | 11-1 | high-speed handpiece | Compliance | 4 | 15
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 15
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 15
Room 11 | 11-4 | ultrasonic scalers | Compliance | 8 | 15
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 15
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 15
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 15
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 15
V1 | V1-1 | high-speed handpiece | Compliance | 3 | 19
V1 | V1-2 | air/water syringes | Compliance | 0 | 19
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 19
V1 | V1-4 | ultrasonic scalers | Compliance | 2 | 19
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 19
V2 | V2-2 | air/water syringes | Compliance | 0 | 19
V2 | V2-3 | Cup filler outlet | Compliance | 3 | 19
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 19
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 19
V3 | V3-2 | air/water syringes | Compliance | 4 | 19
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 19
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 19
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 19
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 19
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 19
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 19
Room 2 | 2-1 | high-speed handpiece | Compliance | 10 | 19
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 19
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 19
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 19
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 19
Room 3 | 3-2 | air/water syringes | Compliance | 20 | 19
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 19
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 19
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 19
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 19
Room 4 | 4-3 | Cup filler outlet | Compliance | 4 | 19
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 19
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 19
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 19
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 19
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 19
Room 6 | 6-1 | high-speed handpiece | Compliance | 5 | 19
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 19
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 19
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 19
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 19
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 19
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 19
Room 7 | 7-4 | ultrasonic scalers | Compliance | 10 | 19
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 19
Room 8 | 8-2 | air/water syringes | Compliance | 1 | 19
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 19
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 19
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 19
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 19
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 19
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 19
Room 10 | 10-1 | high-speed handpiece | Compliance | 1 | 19
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 19
Room 10 | 10-3 | Cup filler outlet | Compliance | 8 | 19
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 19
Room 11 | 11-1 | high-speed handpiece | Compliance | 5 | 19
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 19
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 19
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 19
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 19
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 19
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 19
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 19
V1 | V1-1 | high-speed handpiece | Compliance | 11 | 23
V1 | V1-2 | air/water syringes | Compliance | 0 | 23
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 23
V1 | V1-4 | ultrasonic scalers | Compliance | 7 | 23
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 23
V2 | V2-2 | air/water syringes | Compliance | 10 | 23
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 23
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 23
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 23
V3 | V3-2 | air/water syringes | Compliance | 0 | 23
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 23
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 23
Room 1 | 1-1 | high-speed handpiece | Compliance | 1 | 23
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 23
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 23
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 23
Room 2 | 2-1 | high-speed handpiece | Compliance | 2 | 23
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 23
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 23
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 23
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 23
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 23
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 23
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 23
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 23
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 23
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 23
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 23
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 23
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 23
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 23
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 23
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 23
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 23
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 23
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 23
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 23
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 23
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 23
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 23
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 23
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 23
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 23
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 23
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 23
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 23
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 23
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 23
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 23
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 23
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 23
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 23
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 23
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 23
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 23
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 23
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 3 | 23
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 23
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 23
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 23
V1 | V1-1 | high-speed handpiece | Compliance | 1 | 27
V1 | V1-2 | air/water syringes | Compliance | 20 | 27
V1 | V1-3 | Cup filler outlet | Compliance | 10 | 27
V1 | V1-4 | ultrasonic scalers | Compliance | 5 | 27
V2 | V2-1 | high-speed handpiece | Non-compliance | 600 | 27
V2 | V2-2 | air/water syringes | Compliance | 0 | 27
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 27
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 27
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 27
V3 | V3-2 | air/water syringes | Compliance | 0 | 27
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 27
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 27
Room 1 | 1-1 | high-speed handpiece | Compliance | 1 | 27
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 27
Room 1 | 1-3 | Cup filler outlet | Compliance | 5 | 27
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 27
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 27
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 27
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 27
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 27
Room 3 | 3-1 | high-speed handpiece | Compliance | 7 | 27
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 27
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 27
Room 3 | 3-4 | ultrasonic scalers | Compliance | 9 | 27
Room 4 | 4-1 | high-speed handpiece | Compliance | 10 | 27
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 27
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 27
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 27
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 27
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 27
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 27
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 27
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 27
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 27
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 27
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 27
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 27
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 27
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 27
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 27
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 27
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 27
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 27
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 27
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 27
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 27
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 27
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 27
Room 10 | 10-1 | high-speed handpiece | Compliance | 10 | 27
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 27
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 27
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 27
Room 11 | 11-1 | high-speed handpiece | Compliance | 5 | 27
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 27
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 27
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 27
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 27
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 27
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 27
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 27
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 31
V1 | V1-2 | air/water syringes | Compliance | 0 | 31
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 31
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 31
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 31
V2 | V2-2 | air/water syringes | Compliance | 0 | 31
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 31
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 31
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 31
V3 | V3-2 | air/water syringes | Compliance | 0 | 31
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 31
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 31
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 31
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 31
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 31
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 31
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 31
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 31
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 31
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 31
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 31
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 31
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 31
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 31
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 31
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 31
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 31
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 31
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 31
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 31
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 31
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 31
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 31
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 31
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 31
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 31
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 31
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 31
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 31
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 31
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 31
Room 8 | 8-2 | air/water syringes | Compliance | 5 | 31
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 31
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 31
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 31
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 31
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 31
Room 9 | 9-4 | ultrasonic scalers | Compliance | 1 | 31
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 31
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 31
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 31
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 31
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 31
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 31
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 31
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 31
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 31
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 31
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 31
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 31
V1 | V1-1 | high-speed handpiece | Compliance | 10 | 35
V1 | V1-2 | air/water syringes | Compliance | 15 | 35
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 35
V1 | V1-4 | ultrasonic scalers | Compliance | 25 | 35
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 35
V2 | V2-2 | air/water syringes | Compliance | 0 | 35
V2 | V2-3 | Cup filler outlet | Compliance | 10 | 35
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 35
V3 | V3-1 | high-speed handpiece | Compliance | 6 | 35
V3 | V3-2 | air/water syringes | Compliance | 5 | 35
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 35
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 35
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 35
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 35
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 35
Room 1 | 1-4 | ultrasonic scalers | Compliance | 4 | 35
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 35
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 35
Room 2 | 2-3 | Cup filler outlet | Compliance | 5 | 35
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 35
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 35
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 35
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 35
Room 3 | 3-4 | ultrasonic scalers | Compliance | 3 | 35
Room 4 | 4-1 | high-speed handpiece | Compliance | 5 | 35
Room 4 | 4-2 | air/water syringes | Compliance | 1 | 35
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 35
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 35
Room 5 | 5-1 | high-speed handpiece | Compliance | 6 | 35
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 35
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 35
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 35
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 35
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 35
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 35
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 35
Room 7 | 7-1 | high-speed handpiece | Compliance | 200 | 35
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 35
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 35
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 35
Room 8 | 8-1 | high-speed handpiece | Compliance | 20 | 35
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 35
Room 8 | 8-3 | Cup filler outlet | Compliance | 2 | 35
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 35
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 35
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 35
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 35
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 35
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 35
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 35
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 35
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 35
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 35
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 35
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 35
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 35
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 35
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 1 | 35
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 35
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 4 | 35
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 39
V1 | V1-2 | air/water syringes | Compliance | 0 | 39
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 39
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 39
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 39
V2 | V2-2 | air/water syringes | Compliance | 0 | 39
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 39
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 39
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 39
V3 | V3-2 | air/water syringes | Compliance | 0 | 39
V3 | V3-3 | Cup filler outlet | Compliance | 2 | 39
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 39
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 39
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 39
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 39
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 39
Room 2 | 2-1 | high-speed handpiece | Compliance | 20 | 39
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 39
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 39
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 39
Room 3 | 3-1 | high-speed handpiece | Compliance | 10 | 39
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 39
Room 3 | 3-3 | Cup filler outlet | Compliance | 5 | 39
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 39
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 39
Room 4 | 4-2 | air/water syringes | Compliance | 4 | 39
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 39
Room 4 | 4-4 | ultrasonic scalers | Compliance | 10 | 39
Room 5 | 5-1 | high-speed handpiece | Non-compliance | 550 | 39
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 39
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 39
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 39
Room 6 | 6-1 | high-speed handpiece | Compliance | 20 | 39
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 39
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 39
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 39
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 39
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 39
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 39
Room 7 | 7-4 | ultrasonic scalers | Compliance | 10 | 39
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 39
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 39
Room 8 | 8-3 | Cup filler outlet | Compliance | 5 | 39
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 39
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 39
Room 9 | 9-2 | air/water syringes | Compliance | 3 | 39
Room 9 | 9-3 | Cup filler outlet | Compliance | 6 | 39
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 39
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 39
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 39
Room 10 | 10-3 | Cup filler outlet | Compliance | 5 | 39
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 39
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 39
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 39
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 39
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 39
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 2 | 39
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 39
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 39
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 39
V1 | V1-1 | high-speed handpiece | Compliance | 5 | 43
V1 | V1-2 | air/water syringes | Compliance | 10 | 43
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 43
V1 | V1-4 | ultrasonic scalers | Compliance | 5 | 43
V2 | V2-1 | high-speed handpiece | Compliance | 5 | 43
V2 | V2-2 | air/water syringes | Compliance | 0 | 43
V2 | V2-3 | Cup filler outlet | Compliance | 6 | 43
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 43
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 43
V3 | V3-2 | air/water syringes | Compliance | 0 | 43
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 43
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 43
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 43
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 43
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 43
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 43
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 43
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 43
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 43
Room 2 | 2-4 | ultrasonic scalers | Compliance | 5 | 43
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 43
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 43
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 43
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 43
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 43
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 43
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 43
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 43
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 43
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 43
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 43
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 43
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 43
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 43
Room 6 | 6-3 | Cup filler outlet | Compliance | 5 | 43
Room 6 | 6-4 | ultrasonic scalers | Compliance | 8 | 43
Room 7 | 7-1 | high-speed handpiece | Compliance | 19 | 43
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 43
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 43
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 43
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 43
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 43
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 43
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 43
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 43
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 43
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 43
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 43
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 43
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 43
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 43
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 43
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 43
Room 11 | 11-2 | air/water syringes | Compliance | 5 | 43
Room 11 | 11-3 | Cup filler outlet | Compliance | 5 | 43
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 43
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 43
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 43
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 43
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 43
V1 | V1-1 | high-speed handpiece | Compliance | 10 | 47
V1 | V1-2 | air/water syringes | Non-compliance | 550 | 47
V1 | V1-3 | Cup filler outlet | Compliance | 20 | 47
V1 | V1-4 | ultrasonic scalers | Non-compliance | 600 | 47
V2 | V2-1 | high-speed handpiece | Compliance | 2 | 47
V2 | V2-2 | air/water syringes | Compliance | 3 | 47
V2 | V2-3 | Cup filler outlet | Compliance | 4 | 47
V2 | V2-4 | ultrasonic scalers | Compliance | 4 | 47
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 47
V3 | V3-2 | air/water syringes | Compliance | 0 | 47
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 47
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 47
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 47
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 47
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 47
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 47
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 47
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 47
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 47
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 47
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 47
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 47
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 47
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 47
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 47
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 47
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 47
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 47
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 47
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 47
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 47
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 47
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 47
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 47
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 47
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 47
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 47
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 47
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 47
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 47
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 47
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 47
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 47
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 47
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 47
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 47
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 47
Room 9 | 9-4 | ultrasonic scalers | Compliance | 10 | 47
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 47
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 47
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 47
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 47
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 47
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 47
Room 11 | 11-3 | Cup filler outlet | Compliance | 10 | 47
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 47
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 47
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 47
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 47
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 47
V1 | V1-1 | high-speed handpiece | Compliance | 0 | 51
V1 | V1-2 | air/water syringes | Compliance | 0 | 51
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 51
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 51
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 51
V2 | V2-2 | air/water syringes | Compliance | 0 | 51
V2 | V2-3 | Cup filler outlet | Compliance | 0 | 51
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 51
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 51
V3 | V3-2 | air/water syringes | Compliance | 0 | 51
V3 | V3-3 | Cup filler outlet | Compliance | 0 | 51
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 51
Room 1 | 1-1 | high-speed handpiece | Compliance | 5 | 51
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 51
Room 1 | 1-3 | Cup filler outlet | Compliance | 5 | 51
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 51
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 51
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 51
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 51
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 51
Room 3 | 3-1 | high-speed handpiece | Compliance | 20 | 51
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 51
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 51
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 51
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 51
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 51
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 51
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 51
Room 5 | 5-1 | high-speed handpiece | Compliance | 10 | 51
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 51
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 51
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 51
Room 6 | 6-1 | high-speed handpiece | Compliance | 5 | 51
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 51
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 51
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 51
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 51
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 51
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 51
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 51
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 51
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 51
Room 8 | 8-3 | Cup filler outlet | Compliance | 10 | 51
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 51
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 51
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 51
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 51
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 51
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 51
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 51
Room 10 | 10-3 | Cup filler outlet | Compliance | 0 | 51
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 51
Room 11 | 11-1 | high-speed handpiece | Compliance | 0 | 51
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 51
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 51
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 51
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 51
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 51
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 51
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 51
V1 | V1-1 | high-speed handpiece | Non-compliance | 750 | 55
V1 | V1-2 | air/water syringes | Compliance | 0 | 55
V1 | V1-3 | Cup filler outlet | Compliance | 0 | 55
V1 | V1-4 | ultrasonic scalers | Compliance | 0 | 55
V2 | V2-1 | high-speed handpiece | Compliance | 0 | 55
V2 | V2-2 | air/water syringes | Compliance | 0 | 55
V2 | V2-3 | Cup filler outlet | Compliance | 6 | 55
V2 | V2-4 | ultrasonic scalers | Compliance | 0 | 55
V3 | V3-1 | high-speed handpiece | Compliance | 0 | 55
V3 | V3-2 | air/water syringes | Compliance | 10 | 55
V3 | V3-3 | Cup filler outlet | Compliance | 3 | 55
V3 | V3-4 | ultrasonic scalers | Compliance | 0 | 55
Room 1 | 1-1 | high-speed handpiece | Compliance | 0 | 55
Room 1 | 1-2 | air/water syringes | Compliance | 0 | 55
Room 1 | 1-3 | Cup filler outlet | Compliance | 0 | 55
Room 1 | 1-4 | ultrasonic scalers | Compliance | 0 | 55
Room 2 | 2-1 | high-speed handpiece | Compliance | 0 | 55
Room 2 | 2-2 | air/water syringes | Compliance | 0 | 55
Room 2 | 2-3 | Cup filler outlet | Compliance | 0 | 55
Room 2 | 2-4 | ultrasonic scalers | Compliance | 0 | 55
Room 3 | 3-1 | high-speed handpiece | Compliance | 0 | 55
Room 3 | 3-2 | air/water syringes | Compliance | 0 | 55
Room 3 | 3-3 | Cup filler outlet | Compliance | 0 | 55
Room 3 | 3-4 | ultrasonic scalers | Compliance | 0 | 55
Room 4 | 4-1 | high-speed handpiece | Compliance | 0 | 55
Room 4 | 4-2 | air/water syringes | Compliance | 0 | 55
Room 4 | 4-3 | Cup filler outlet | Compliance | 0 | 55
Room 4 | 4-4 | ultrasonic scalers | Compliance | 0 | 55
Room 5 | 5-1 | high-speed handpiece | Compliance | 0 | 55
Room 5 | 5-2 | air/water syringes | Compliance | 0 | 55
Room 5 | 5-3 | Cup filler outlet | Compliance | 0 | 55
Room 5 | 5-4 | ultrasonic scalers | Compliance | 0 | 55
Room 6 | 6-1 | high-speed handpiece | Compliance | 0 | 55
Room 6 | 6-2 | air/water syringes | Compliance | 0 | 55
Room 6 | 6-3 | Cup filler outlet | Compliance | 0 | 55
Room 6 | 6-4 | ultrasonic scalers | Compliance | 0 | 55
Room 7 | 7-1 | high-speed handpiece | Compliance | 0 | 55
Room 7 | 7-2 | air/water syringes | Compliance | 0 | 55
Room 7 | 7-3 | Cup filler outlet | Compliance | 0 | 55
Room 7 | 7-4 | ultrasonic scalers | Compliance | 0 | 55
Room 8 | 8-1 | high-speed handpiece | Compliance | 0 | 55
Room 8 | 8-2 | air/water syringes | Compliance | 0 | 55
Room 8 | 8-3 | Cup filler outlet | Compliance | 0 | 55
Room 8 | 8-4 | ultrasonic scalers | Compliance | 0 | 55
Room 9 | 9-1 | high-speed handpiece | Compliance | 0 | 55
Room 9 | 9-2 | air/water syringes | Compliance | 0 | 55
Room 9 | 9-3 | Cup filler outlet | Compliance | 0 | 55
Room 9 | 9-4 | ultrasonic scalers | Compliance | 0 | 55
Room 10 | 10-1 | high-speed handpiece | Compliance | 0 | 55
Room 10 | 10-2 | air/water syringes | Compliance | 0 | 55
Room 10 | 10-3 | Cup filler outlet | Compliance | 6 | 55
Room 10 | 10-4 | ultrasonic scalers | Compliance | 0 | 55
Room 11 | 11-1 | high-speed handpiece | Non-compliance | 600 | 55
Room 11 | 11-2 | air/water syringes | Compliance | 0 | 55
Room 11 | 11-3 | Cup filler outlet | Compliance | 0 | 55
Room 11 | 11-4 | ultrasonic scalers | Compliance | 0 | 55
种植牙手术室 | 种植牙手术室-1 | high-speed handpiece | Compliance | 0 | 55
种植牙手术室 | 种植牙手术室-2 | air/water syringes | Compliance | 0 | 55
种植牙手术室 | 种植牙手术室-3 | Cup filler outlet | Compliance | 0 | 55
种植牙手术室 | 种植牙手术室-4 | ultrasonic scalers | Compliance | 0 | 55

## mNGS-bacteria
Sample | group1 | group2 | Latin | Chinese | Coverage | CovRate | Depth | GenusLatin | GenusChi | Latin_smrn | G_SMRN | Latin_Re_Abu | Genus_Re_Abu | Latin_mrn | G_MRN | SDLatin_mrn | SDLatin_smrn | SDG_MRN | SDG_SMRN | Gram | Latin_Abs_Abu | Genus_Abs_Abu | Depth_Ratio | Shannon_index | RefID | LatinID
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_sp._BTAi1 | 慢生根瘤菌BTAi1 |  | 37.92 | 1.5 | Bradyrhizobium | 慢生根瘤菌属 | 58975 | 106933 | 31.91 | 59.1 | 111989 | 208028 | 36903 | 19434 | 68550 | 35237 | G- | 223.2576 | 413.557 | 0.88 | 1 | id¦39765305¦BAC¦R_9966658¦ | id¦83252480¦BAC¦S_8337294¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_lablabi | 扁豆慢生根瘤菌 |  | 2.72 | 1.15 | Bradyrhizobium | 慢生根瘤菌属 | 1714 | 106933 | 3.8 | 59.1 | 13157 | 208028 | 4336 | 565 | 68550 | 35237 | G- | 26.5956 | 413.557 | 0.89 | 1 | id¦79007734¦BAC¦R_2354119¦ | id¦00811465¦BAC¦S_5469420¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_betae | 甜菜慢生根瘤菌 |  | 2.32 | 2.14 | Bradyrhizobium | 慢生根瘤菌属 | 6524 | 106933 | 3.11 | 59.1 | 9435 | 208028 | 3109 | 2150 | 68550 | 35237 | G- | 21.7414 | 413.557 | 0.48 | 0.43 | id¦82318762¦BAC¦R_0551035¦ | id¦88323034¦BAC¦S_0661593¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_oligotrophicum | 寡养慢生根瘤菌 |  | 3.39 | 1.21 | Bradyrhizobium | 慢生根瘤菌属 | 787 | 106933 | 2.34 | 59.1 | 8198 | 208028 | 2701 | 259 | 68550 | 35237 | G- | 16.3443 | 413.557 | 0.84 | 1 | id¦33180995¦BAC¦R_5105019¦ | id¦16673924¦BAC¦S_7669691¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_sp._ORS_278 | 慢生根瘤菌ORS278 |  | 3.26 | 1.22 | Bradyrhizobium | 慢生根瘤菌属 | 433 | 106933 | 2.25 | 59.1 | 7130 | 208028 | 2350 | 143 | 68550 | 35237 | G- | 15.7546 | 413.557 | 0.84 | 1 | id¦90664589¦BAC¦R_9847007¦ | id¦20386990¦BAC¦S_9436128¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_elkanii | 埃氏慢生根瘤菌 |  | 0.8646 | 1.58 | Bradyrhizobium | 慢生根瘤菌属 | 858 | 106933 | 1.76 | 59.1 | 7141 | 208028 | 2353 | 283 | 68550 | 35237 | G- | 12.3224 | 413.557 | 0.64 | 0.91 | id¦82867196¦BAC¦R_3373169¦ | id¦73364065¦BAC¦S_4260681¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_japonicum | 日本慢生根瘤菌 |  | 0.8958 | 1.37 | Bradyrhizobium | 慢生根瘤菌属 | 800 | 106933 | 1.69 | 59.1 | 5434 | 208028 | 1791 | 264 | 68550 | 35237 | G- | 11.7954 | 413.557 | 0.74 | 0.96 | id¦07535899¦BAC¦R_5672879¦ | id¦27841201¦BAC¦S_3037239¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_guangdongense | 广东慢生根瘤菌 |  | 1.08 | 1.2 | Bradyrhizobium | 慢生根瘤菌属 | 314 | 106933 | 1.57 | 59.1 | 4512 | 208028 | 1487 | 103 | 68550 | 35237 | G- | 11.0091 | 413.557 | 0.84 | 1 | id¦29608961¦BAC¦R_6141532¦ | id¦63190979¦BAC¦S_1365294¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_erythrophlei | 格木慢生根瘤菌 |  | 0.7283 | 1.26 | Bradyrhizobium | 慢生根瘤菌属 | 364 | 106933 | 1.35 | 59.1 | 6743 | 208028 | 2222 | 120 | 68550 | 35237 | G- | 9.4644 | 413.557 | 0.79 | 1 | id¦22278535¦BAC¦R_3333209¦ | id¦73827760¦BAC¦S_8098722¦
E | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_valentinum | 慢生根瘤菌* |  | 1.03 | 1.64 | Bradyrhizobium | 慢生根瘤菌属 | 910 | 106933 | 0.96 | 59.1 | 3734 | 208028 | 1230 | 300 | 68550 | 35237 | G- | 6.7246 | 413.557 | 0.61 | 0.91 | id¦35529185¦BAC¦R_8283032¦ | id¦48144680¦BAC¦S_1351439¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_sp._BTAi1 | 慢生根瘤菌BTAi1 |  | 5.56 | 1.05 | Bradyrhizobium | 慢生根瘤菌属 | 6394 | 12001 | 29.75 | 55.95 | 11830 | 22327 | 16162 | 8735 | 30502 | 16395 | G- | 97.7762 | 183.8456 | 0.98 | 0.99 | id¦39765305¦BAC¦R_9966658¦ | id¦83252480¦BAC¦S_8337294¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_lablabi | 扁豆慢生根瘤菌 |  | 0.6817 | 1.02 | Bradyrhizobium | 慢生根瘤菌属 | 414 | 12001 | 5.46 | 55.95 | 2140 | 22327 | 2924 | 566 | 30502 | 16395 | G- | 17.9343 | 183.8456 | 0.98 | 1 | id¦79007734¦BAC¦R_2354119¦ | id¦00811465¦BAC¦S_5469420¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_betae | 甜菜慢生根瘤菌 |  | 0.4521 | 1.13 | Bradyrhizobium | 慢生根瘤菌属 | 699 | 12001 | 2.88 | 55.95 | 989 | 22327 | 1351 | 955 | 30502 | 16395 | G- | 9.4484 | 183.8456 | 0.89 | 0.44 | id¦82318762¦BAC¦R_0551035¦ | id¦88323034¦BAC¦S_0661593¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_oligotrophicum | 寡养慢生根瘤菌 |  | 0.3918 | 1.03 | Bradyrhizobium | 慢生根瘤菌属 | 89 | 12001 | 2.06 | 55.95 | 820 | 22327 | 1120 | 122 | 30502 | 16395 | G- | 6.7778 | 183.8456 | 0.98 | 0.99 | id¦33180995¦BAC¦R_5105019¦ | id¦16673924¦BAC¦S_7669691¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_sp._ORS_278 | 慢生根瘤菌ORS278 |  | 0.3655 | 1.02 | Bradyrhizobium | 慢生根瘤菌属 | 48 | 12001 | 1.92 | 55.95 | 688 | 22327 | 940 | 66 | 30502 | 16395 | G- | 6.3027 | 183.8456 | 0.98 | 0.99 | id¦90664589¦BAC¦R_9847007¦ | id¦20386990¦BAC¦S_9436128¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_elkanii | 埃氏慢生根瘤菌 |  | 0.1156 | 1.23 | Bradyrhizobium | 慢生根瘤菌属 | 111 | 12001 | 1.6 | 55.95 | 734 | 22327 | 1003 | 152 | 30502 | 16395 | G- | 5.2511 | 183.8456 | 0.81 | 0.89 | id¦82867196¦BAC¦R_3373169¦ | id¦73364065¦BAC¦S_4260681¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_japonicum | 日本慢生根瘤菌 |  | 0.1111 | 1.06 | Bradyrhizobium | 慢生根瘤菌属 | 100 | 12001 | 1.42 | 55.95 | 518 | 22327 | 708 | 137 | 30502 | 16395 | G- | 4.6616 | 183.8456 | 0.94 | 0.94 | id¦07535899¦BAC¦R_5672879¦ | id¦27841201¦BAC¦S_3037239¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_erythrophlei | 格木慢生根瘤菌 |  | 0.094 | 1.02 | Bradyrhizobium | 慢生根瘤菌属 | 43 | 12001 | 1.28 | 55.95 | 724 | 22327 | 989 | 59 | 30502 | 16395 | G- | 4.2131 | 183.8456 | 0.98 | 0.98 | id¦22278535¦BAC¦R_3333209¦ | id¦73827760¦BAC¦S_8098722¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_guangdongense | 广东慢生根瘤菌 |  | 0.1062 | 1.03 | Bradyrhizobium | 慢生根瘤菌属 | 36 | 12001 | 1.28 | 55.95 | 415 | 22327 | 567 | 49 | 30502 | 16395 | G- | 4.198 | 183.8456 | 0.97 | 1 | id¦29608961¦BAC¦R_6141532¦ | id¦63190979¦BAC¦S_1365294¦
B | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_valentinum | 慢生根瘤菌* |  | 0.1797 | 1.07 | Bradyrhizobium | 慢生根瘤菌属 | 91 | 12001 | 1 | 55.95 | 438 | 22327 | 598 | 124 | 30502 | 16395 | G- | 3.2702 | 183.8456 | 0.93 | 0.91 | id¦35529185¦BAC¦R_8283032¦ | id¦48144680¦BAC¦S_1351439¦
R252 | Terminal outlets After Disinfection | After Disinfection | Phyllobacterium_myrsinacearum | 紫金牛叶杆菌 |  | 2.84 | 1.04 | Phyllobacterium | 叶杆菌属 | 1726 | 1897 | 33.85 | 35.75 | 3874 | 4094 | 1733 | 772 | 1831 | 848 | G- | 15.4965 | 16.3663 | 0.97 | 0.94 | id¦32375896¦BAC¦R_3175210¦ | id¦71697530¦BAC¦S_9673816¦
G | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_sp._BTAi1 | 慢生根瘤菌BTAi1 |  | 0.4489 | 1 | Bradyrhizobium | 慢生根瘤菌属 | 484 | 860 | 19.5 | 32.17 | 913 | 1506 | 901 | 478 | 1486 | 849 | G- | 5.4501 | 8.9914 | 1 | 1 | id¦39765305¦BAC¦R_9966658¦ | id¦83252480¦BAC¦S_8337294¦
G | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_lablabi | 扁豆慢生根瘤菌 |  | 0.0339 | 1 | Bradyrhizobium | 慢生根瘤菌属 | 24 | 860 | 2.25 | 32.17 | 104 | 1506 | 103 | 24 | 1486 | 849 | G- | 0.6295 | 8.9914 | 1 | 0.99 | id¦79007734¦BAC¦R_2354119¦ | id¦00811465¦BAC¦S_5469420¦
G | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_oligotrophicum | 寡养慢生根瘤菌 |  | 0.0373 | 1 | Bradyrhizobium | 慢生根瘤菌属 | 13 | 860 | 1.62 | 32.17 | 76 | 1506 | 75 | 13 | 1486 | 849 | G- | 0.4537 | 8.9914 | 1 | 1 | id¦33180995¦BAC¦R_5105019¦ | id¦16673924¦BAC¦S_7669691¦
G | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_betae | 甜菜慢生根瘤菌 |  | 0.0241 | 1.02 | Bradyrhizobium | 慢生根瘤菌属 | 30 | 860 | 1.28 | 32.17 | 52 | 1506 | 51 | 30 | 1486 | 849 | G- | 0.3588 | 8.9914 | 0.98 | 0.45 | id¦82318762¦BAC¦R_0551035¦ | id¦88323034¦BAC¦S_0661593¦
G | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_japonicum | 日本慢生根瘤菌 |  | 0.0113 | 1 | Bradyrhizobium | 慢生根瘤菌属 | 14 | 860 | 0.88 | 32.17 | 38 | 1506 | 37 | 14 | 1486 | 849 | G- | 0.247 | 8.9914 | 1 | 0.7 | id¦07535899¦BAC¦R_5672879¦ | id¦27841201¦BAC¦S_3037239¦
R248 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_acnes | 痤疮丙酸杆菌 |  | 0.4471 | 1 | Cutibacterium | - | 247 | 318 | 21.16 | 22.33 | 313 | 328 | 435 | 343 | 456 | 442 | G+ | 7.8627 | 8.2996 | 1 | 1 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
R253 | Terminal outlets After Disinfection | After Disinfection | Phyllobacterium_myrsinacearum | 紫金牛叶杆菌 |  | 3.14 | 1.04 | Phyllobacterium | 叶杆菌属 | 2258 | 2497 | 21.05 | 22.02 | 4487 | 4700 | 3726 | 1875 | 3903 | 2073 | G- | 33.3194 | 34.8536 | 0.98 | 0.95 | id¦32375896¦BAC¦R_3175210¦ | id¦71697530¦BAC¦S_9673816¦
R252 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_acnes | 痤疮丙酸杆菌 |  | 1.2 | 1.02 | Cutibacterium | - | 854 | 1072 | 19.28 | 20.86 | 1092 | 1172 | 488 | 382 | 524 | 479 | G+ | 8.823 | 9.5474 | 0.99 | 0.98 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
R252 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_avidum | - |  | 0.0347 | 1 | Cutibacterium | - | 14 | 1072 | 0.54 | 20.86 | 30 | 1172 | 13 | 6 | 524 | 479 | G+ | 0.2461 | 9.5474 | 1 | 0.94 | id¦53354550¦BAC¦R_2931644¦ | id¦18251146¦BAC¦S_8963193¦
R252 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_granulosum | - |  | 0.0439 | 1.02 | Cutibacterium | - | 15 | 1072 | 0.52 | 20.86 | 23 | 1172 | 10 | 7 | 524 | 479 | G+ | 0.2365 | 9.5474 | 0.98 | 0.98 | id¦77522930¦BAC¦R_0272957¦ | id¦05220705¦BAC¦S_7001618¦
E | Terminal outlets Before Disinfection | Before Disinfection | Hydrotalea_flava | - |  | 17.8 | 1.13 | Hydrotalea | - | 13582 | 13898 | 20.64 | 20.84 | 15369 | 15645 | 5064 | 4476 | 5155 | 4580 | G- | 144.4207 | 145.8144 | 0.98 | 1 | id¦35807908¦BAC¦R_2583170¦ | id¦94051955¦BAC¦S_8621411¦
E | Terminal outlets Before Disinfection | Before Disinfection | Hydrotalea_sandarakina | - |  | 0.3304 | 1.06 | Hydrotalea | - | 67 | 13898 | 0.2 | 20.84 | 276 | 15645 | 91 | 22 | 5155 | 4580 | G- | 1.3937 | 145.8144 | 0.95 | 0.95 | id¦67914098¦BAC¦R_4600360¦ | id¦08121401¦BAC¦S_7500808¦
R253 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_acnes | 痤疮丙酸杆菌 |  | 2.49 | 1.01 | Cutibacterium | - | 1447 | 1881 | 17.73 | 19.03 | 1871 | 1992 | 1554 | 1201 | 1654 | 1562 | G+ | 28.0631 | 30.1217 | 1 | 0.98 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
R253 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_granulosum | - |  | 0.0789 | 1 | Cutibacterium | - | 34 | 1881 | 0.51 | 19.03 | 42 | 1992 | 35 | 28 | 1654 | 1562 | G+ | 0.8016 | 30.1217 | 1 | 1 | id¦77522930¦BAC¦R_0272957¦ | id¦05220705¦BAC¦S_7001618¦
R253 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_avidum | - |  | 0.0418 | 1 | Cutibacterium | - | 18 | 1881 | 0.37 | 19.03 | 38 | 1992 | 32 | 15 | 1654 | 1562 | G+ | 0.5786 | 30.1217 | 1 | 0.93 | id¦53354550¦BAC¦R_2931644¦ | id¦18251146¦BAC¦S_8963193¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_sp._BTAi1 | 慢生根瘤菌BTAi1 |  | 8.3 | 1.08 | Bradyrhizobium | 慢生根瘤菌属 | 9844 | 16464 | 9.8 | 15.56 | 18040 | 28674 | 8497 | 4637 | 13506 | 7755 | G- | 51.4059 | 81.6211 | 0.97 | 1 | id¦39765305¦BAC¦R_9966658¦ | id¦83252480¦BAC¦S_8337294¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_lablabi | 扁豆慢生根瘤菌 |  | 0.4621 | 1.02 | Bradyrhizobium | 慢生根瘤菌属 | 247 | 16464 | 0.88 | 15.56 | 1599 | 28674 | 753 | 116 | 13506 | 7755 | G- | 4.6201 | 81.6211 | 0.99 | 1 | id¦79007734¦BAC¦R_2354119¦ | id¦00811465¦BAC¦S_5469420¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_oligotrophicum | 寡养慢生根瘤菌 |  | 0.5418 | 1.03 | Bradyrhizobium | 慢生根瘤菌属 | 110 | 16464 | 0.62 | 15.56 | 1143 | 28674 | 538 | 52 | 13506 | 7755 | G- | 3.2572 | 81.6211 | 0.97 | 1 | id¦33180995¦BAC¦R_5105019¦ | id¦16673924¦BAC¦S_7669691¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_sp._ORS_278 | 慢生根瘤菌ORS278 |  | 0.5291 | 1.04 | Bradyrhizobium | 慢生根瘤菌属 | 75 | 16464 | 0.61 | 15.56 | 1011 | 28674 | 476 | 35 | 13506 | 7755 | G- | 3.1931 | 81.6211 | 0.97 | 1 | id¦90664589¦BAC¦R_9847007¦ | id¦20386990¦BAC¦S_9436128¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_betae | 甜菜慢生根瘤菌 |  | 0.4443 | 1.12 | Bradyrhizobium | 慢生根瘤菌属 | 660 | 16464 | 0.6 | 15.56 | 958 | 28674 | 451 | 311 | 13506 | 7755 | G- | 3.1554 | 81.6211 | 0.89 | 0.41 | id¦82318762¦BAC¦R_0551035¦ | id¦88323034¦BAC¦S_0661593¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_japonicum | 日本慢生根瘤菌 |  | 0.1424 | 1.03 | Bradyrhizobium | 慢生根瘤菌属 | 107 | 16464 | 0.35 | 15.56 | 591 | 28674 | 278 | 50 | 13506 | 7755 | G- | 1.8337 | 81.6211 | 0.97 | 0.97 | id¦07535899¦BAC¦R_5672879¦ | id¦27841201¦BAC¦S_3037239¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_elkanii | 埃氏慢生根瘤菌 |  | 0.1012 | 1.14 | Bradyrhizobium | 慢生根瘤菌属 | 87 | 16464 | 0.32 | 15.56 | 682 | 28674 | 321 | 41 | 13506 | 7755 | G- | 1.6822 | 81.6211 | 0.87 | 0.94 | id¦82867196¦BAC¦R_3373169¦ | id¦73364065¦BAC¦S_4260681¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_erythrophlei | 格木慢生根瘤菌 |  | 0.0934 | 1.02 | Bradyrhizobium | 慢生根瘤菌属 | 30 | 16464 | 0.28 | 15.56 | 730 | 28674 | 344 | 14 | 13506 | 7755 | G- | 1.4646 | 81.6211 | 0.98 | 0.98 | id¦22278535¦BAC¦R_3333209¦ | id¦73827760¦BAC¦S_8098722¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_valentinum | 慢生根瘤菌* |  | 0.1469 | 1.09 | Bradyrhizobium | 慢生根瘤菌属 | 85 | 16464 | 0.18 | 15.56 | 363 | 28674 | 171 | 40 | 13506 | 7755 | G- | 0.9344 | 81.6211 | 0.92 | 0.91 | id¦35529185¦BAC¦R_8283032¦ | id¦48144680¦BAC¦S_1351439¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bradyrhizobium_cajani | 木豆瘤慢生根瘤菌 |  | 0.0787 | 1.21 | Bradyrhizobium | 慢生根瘤菌属 | 29 | 16464 | 0.11 | 15.56 | 198 | 28674 | 93 | 14 | 13506 | 7755 | G- | 0.5569 | 81.6211 | 0.83 | 0.87 | id¦72617339¦BAC¦R_9875012¦ | id¦92799160¦BAC¦S_7013691¦
R249 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_acnes | 痤疮丙酸杆菌 |  | 2.25 | 1.02 | Cutibacterium | - | 1483 | 1939 | 11.83 | 13.18 | 1859 | 2040 | 1147 | 915 | 1258 | 1196 | G+ | 20.7104 | 23.0721 | 1 | 0.98 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
R249 | Terminal outlets After Disinfection | After Disinfection | Cutibacterium_granulosum | - |  | 0.1296 | 1 | Cutibacterium | - | 53 | 1939 | 0.56 | 13.18 | 69 | 2040 | 43 | 33 | 1258 | 1196 | G+ | 0.9782 | 23.0721 | 1 | 1 | id¦77522930¦BAC¦R_0272957¦ | id¦05220705¦BAC¦S_7001618¦
R249 | Terminal outlets After Disinfection | After Disinfection | [Propionibacterium]_namnetense | - |  | 0.1229 | 1.01 | Cutibacterium | - | 37 | 1939 | 0.54 | 13.18 | 74 | 2040 | 46 | 23 | 1258 | 1196 | G+ | 0.9386 | 23.0721 | 0.99 | 1 | id¦98833027¦BAC¦R_8182154¦ | id¦85186092¦BAC¦S_0590636¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_mitis | 缓症链球菌 |  | 0.7854 | 1 | Streptococcus | 链球菌属 | 251 | 4513 | 2.8 | 12.53 | 1250 | 5673 | 589 | 118 | 2672 | 2126 | G+ | 14.6771 | 65.7489 | 1 | 1 | id¦89924070¦BAC¦R_7367586¦ | id¦71856117¦BAC¦S_5870034¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_oralis | 口腔链球菌 |  | 0.4502 | 1.01 | Streptococcus | 链球菌属 | 193 | 4513 | 1.84 | 12.53 | 790 | 5673 | 372 | 91 | 2672 | 2126 | G+ | 9.6322 | 65.7489 | 1 | 0.99 | id¦24997853¦BAC¦R_1536629¦ | id¦41327418¦BAC¦S_7770086¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_pseudopneumoniae | 假肺炎链球菌 |  | 0.5585 | 1.01 | Streptococcus | 链球菌属 | 87 | 4513 | 1.67 | 12.53 | 800 | 5673 | 377 | 41 | 2672 | 2126 | G+ | 8.7512 | 65.7489 | 0.99 | 0.99 | id¦82178797¦BAC¦R_2499673¦ | id¦20919127¦BAC¦S_3951339¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_parasanguinis | 副血链球菌 |  | 0.3964 | 1.01 | Streptococcus | 链球菌属 | 343 | 4513 | 1.14 | 12.53 | 525 | 5673 | 247 | 162 | 2672 | 2126 | G+ | 5.9834 | 65.7489 | 1 | 1 | id¦77315528¦BAC¦R_4550179¦ | id¦39376444¦BAC¦S_8063262¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_infantis | 婴儿链球菌 |  | 0.3247 | 1.01 | Streptococcus | 链球菌属 | 190 | 4513 | 1.14 | 12.53 | 473 | 5673 | 223 | 89 | 2672 | 2126 | G+ | 5.9611 | 65.7489 | 0.99 | 0.99 | id¦96871594¦BAC¦R_8088358¦ | id¦38632365¦BAC¦S_7649912¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_salivarius | 唾液链球菌 |  | 0.3503 | 1 | Streptococcus | 链球菌属 | 187 | 4513 | 0.88 | 12.53 | 432 | 5673 | 203 | 88 | 2672 | 2126 | G+ | 4.6226 | 65.7489 | 1 | 0.98 | id¦59773801¦BAC¦R_2204183¦ | id¦87078916¦BAC¦S_8037111¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_pneumoniae | 肺炎链球菌 |  | 0.3018 | 1 | Streptococcus | 链球菌属 | 15 | 4513 | 0.45 | 12.53 | 225 | 5673 | 106 | 7 | 2672 | 2126 | G+ | 2.3855 | 65.7489 | 1 | 0.98 | id¦53167892¦BAC¦R_9184812¦ | id¦40596151¦BAC¦S_8428040¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_sp._I-P16 | 链球菌I-P16 |  | 0.1628 | 1 | Streptococcus | 链球菌属 | 29 | 4513 | 0.26 | 12.53 | 113 | 5673 | 53 | 14 | 2672 | 2126 | G+ | 1.3541 | 65.7489 | 1 | 0.99 | id¦49686816¦BAC¦R_4320315¦ | id¦45050604¦BAC¦S_1511555¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_sanguinis | 血链球菌 |  | 0.0797 | 1 | Streptococcus | 链球菌属 | 55 | 4513 | 0.24 | 12.53 | 128 | 5673 | 60 | 26 | 2672 | 2126 | G+ | 1.2779 | 65.7489 | 1 | 0.94 | id¦80290588¦BAC¦R_3199914¦ | id¦24531979¦BAC¦S_9217069¦
D | Terminal outlets Before Disinfection | Before Disinfection | Streptococcus_vestibularis | 前庭链球菌 |  | 0.1088 | 1 | Streptococcus | 链球菌属 | 15 | 4513 | 0.22 | 12.53 | 95 | 5673 | 45 | 7 | 2672 | 2126 | G+ | 1.179 | 65.7489 | 1 | 0.96 | id¦80831820¦BAC¦R_6789889¦ | id¦24720556¦BAC¦S_7802260¦
B | Terminal outlets Before Disinfection | Before Disinfection | Hydrotalea_flava | - |  | 1.3 | 1.01 | Hydrotalea | - | 912 | 932 | 12.12 | 12.24 | 1022 | 1041 | 1396 | 1246 | 1422 | 1273 | G- | 39.8155 | 40.2133 | 1 | 1 | id¦35807908¦BAC¦R_2583170¦ | id¦94051955¦BAC¦S_8621411¦
D | Terminal outlets Before Disinfection | Before Disinfection | Neisseria_subflava | 微黄奈瑟菌 |  | 1.13 | 1.01 | Neisseria | 奈瑟菌属 | 76 | 3068 | 3.05 | 9.36 | 1492 | 4924 | 703 | 36 | 2319 | 1445 | G- | 16.0032 | 49.0901 | 1 | 0.99 | id¦22010104¦BAC¦R_9015187¦ | id¦51793239¦BAC¦S_6138147¦
D | Terminal outlets Before Disinfection | Before Disinfection | Neisseria_flavescens | 浅黄奈瑟菌 |  | 0.7756 | 1.01 | Neisseria | 奈瑟菌属 | 63 | 3068 | 1.71 | 9.36 | 856 | 4924 | 403 | 30 | 2319 | 1445 | G- | 8.9587 | 49.0901 | 1 | 1 | id¦19135610¦BAC¦R_7481958¦ | id¦02704742¦BAC¦S_3424993¦
D | Terminal outlets Before Disinfection | Before Disinfection | Neisseria_mucosa | 黏膜奈瑟菌 |  | 0.5363 | 1.01 | Neisseria | 奈瑟菌属 | 56 | 3068 | 1.47 | 9.36 | 912 | 4924 | 430 | 26 | 2319 | 1445 | G- | 7.715 | 49.0901 | 0.99 | 1 | id¦77161260¦BAC¦R_1905019¦ | id¦11474027¦BAC¦S_6923361¦
D | Terminal outlets Before Disinfection | Before Disinfection | Neisseria_sicca | 干燥奈瑟菌 |  | 0.5022 | 1.01 | Neisseria | 奈瑟菌属 | 81 | 3068 | 1.38 | 9.36 | 755 | 4924 | 356 | 38 | 2319 | 1445 | G- | 7.2252 | 49.0901 | 1 | 0.99 | id¦13875366¦BAC¦R_5467051¦ | id¦69647433¦BAC¦S_0037877¦
D | Terminal outlets Before Disinfection | Before Disinfection | Neisseria_elongata | 长奈瑟菌 |  | 0.1835 | 1 | Neisseria | 奈瑟菌属 | 99 | 3068 | 0.38 | 9.36 | 216 | 4924 | 102 | 47 | 2319 | 1445 | G- | 2.007 | 49.0901 | 1 | 0.98 | id¦02984824¦BAC¦R_6366477¦ | id¦31575720¦BAC¦S_5376443¦
D | Terminal outlets Before Disinfection | Before Disinfection | Neisseria_bacilliformis | 杆状奈瑟菌 |  | 0.0327 | 1 | Neisseria | 奈瑟菌属 | 22 | 3068 | 0.06 | 9.36 | 32 | 4924 | 15 | 10 | 2319 | 1445 | G- | 0.3023 | 49.0901 | 1 | 0.97 | id¦03296529¦BAC¦R_5434640¦ | id¦15388208¦BAC¦S_6314482¦
R249 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_hominis | 人葡萄球菌 |  | 0.143 | 1.01 | Staphylococcus | 葡萄球菌属 | 95 | 1182 | 0.9 | 8.54 | 119 | 1321 | 73 | 59 | 815 | 729 | G+ | 1.5676 | 14.9442 | 0.99 | 1 | id¦58178458¦BAC¦R_6499156¦ | id¦01588904¦BAC¦S_1607535¦
R249 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_aureus | 金黄色葡萄球菌 |  | 0.0953 | 1.01 | Staphylococcus | 葡萄球菌属 | 15 | 1182 | 0.19 | 8.54 | 104 | 1321 | 64 | 9 | 815 | 729 | G+ | 1.0306 | 14.9442 | 0.99 | 0.99 | id¦10808207¦BAC¦R_3968458¦ | id¦57618172¦BAC¦S_1289868¦
R249 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_epidermidis | 表皮葡萄球菌 |  | 0.0483 | 1 | Staphylococcus | 葡萄球菌属 | 35 | 1182 | 0.26 | 8.54 | 41 | 1321 | 25 | 22 | 815 | 729 | G+ | 0.4527 | 14.9442 | 1 | 0.95 | id¦15608884¦BAC¦R_9898902¦ | id¦81948656¦BAC¦S_6145183¦
R249 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_capitis | 头葡萄球菌 |  | 0.031 | 1 | Staphylococcus | 葡萄球菌属 | 12 | 1182 | 0.14 | 8.54 | 19 | 1321 | 12 | 7 | 815 | 729 | G+ | 0.2374 | 14.9442 | 1 | 1 | id¦91254114¦BAC¦R_4675524¦ | id¦78222658¦BAC¦S_6642837¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_melaninogenica | 产黑色普雷沃菌 |  | 0.8641 | 1.01 | Prevotella | 普雷沃菌属 | 687 | 3863 | 1.75 | 6.73 | 1237 | 4669 | 583 | 324 | 2199 | 1820 | G- | 9.1949 | 35.2967 | 1 | 1 | id¦88178094¦BAC¦R_9080140¦ | id¦61369871¦BAC¦S_1570876¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_jejuni | 空肠普雷沃菌 |  | 0.5363 | 1.01 | Prevotella | 普雷沃菌属 | 305 | 3863 | 0.59 | 6.73 | 518 | 4669 | 244 | 144 | 2199 | 1820 | G- | 3.1176 | 35.2967 | 1 | 1 | id¦85620277¦BAC¦R_8343336¦ | id¦26457927¦BAC¦S_6206053¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_pallens | 苍白普雷沃菌 |  | 0.3923 | 1.01 | Prevotella | 普雷沃菌属 | 264 | 3863 | 0.53 | 6.73 | 369 | 4669 | 174 | 124 | 2199 | 1820 | G- | 2.7954 | 35.2967 | 1 | 0.99 | id¦01984445¦BAC¦R_8214264¦ | id¦65342769¦BAC¦S_9539321¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_veroralis | 真口普雷沃菌 |  | 0.3201 | 1 | Prevotella | 普雷沃菌属 | 200 | 3863 | 0.49 | 6.73 | 308 | 4669 | 145 | 94 | 2199 | 1820 | G- | 2.5516 | 35.2967 | 1 | 0.96 | id¦55835549¦BAC¦R_4325770¦ | id¦64206983¦BAC¦S_8300163¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_histicola | 栖组织普雷沃菌 |  | 0.2713 | 1 | Prevotella | 普雷沃菌属 | 229 | 3863 | 0.47 | 6.73 | 318 | 4669 | 150 | 108 | 2199 | 1820 | G- | 2.4566 | 35.2967 | 1 | 1 | id¦29346480¦BAC¦R_1672806¦ | id¦54869476¦BAC¦S_7805381¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_nigrescens | 变黑普雷沃菌 |  | 0.2249 | 1.01 | Prevotella | 普雷沃菌属 | 126 | 3863 | 0.36 | 6.73 | 216 | 4669 | 102 | 59 | 2199 | 1820 | G- | 1.8729 | 35.2967 | 0.99 | 0.99 | id¦59048504¦BAC¦R_7477457¦ | id¦18735548¦BAC¦S_0004225¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_salivae | 唾液普雷沃菌 |  | 0.2349 | 1 | Prevotella | 普雷沃菌属 | 183 | 3863 | 0.33 | 6.73 | 231 | 4669 | 109 | 86 | 2199 | 1820 | G- | 1.7366 | 35.2967 | 1 | 1 | id¦05463120¦BAC¦R_0031378¦ | id¦94593696¦BAC¦S_4324435¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_nanceiensis | 南锡普雷沃菌 |  | 0.2975 | 1 | Prevotella | 普雷沃菌属 | 123 | 3863 | 0.33 | 6.73 | 194 | 4669 | 91 | 58 | 2199 | 1820 | G- | 1.7249 | 35.2967 | 1 | 0.99 | id¦49218625¦BAC¦R_9401929¦ | id¦72362695¦BAC¦S_6143791¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_intermedia | 中间普雷沃菌 |  | 0.1245 | 1 | Prevotella | 普雷沃菌属 | 93 | 3863 | 0.33 | 6.73 | 233 | 4669 | 110 | 44 | 2199 | 1820 | G- | 1.743 | 35.2967 | 1 | 1 | id¦36331089¦BAC¦R_0594071¦ | id¦44925120¦BAC¦S_5588591¦
D | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_oris | 口腔普雷沃菌 |  | 0.1359 | 1 | Prevotella | 普雷沃菌属 | 122 | 3863 | 0.24 | 6.73 | 173 | 4669 | 81 | 57 | 2199 | 1820 | G- | 1.2558 | 35.2967 | 1 | 0.98 | id¦17571059¦BAC¦R_2645811¦ | id¦59992893¦BAC¦S_3571883¦
G | Terminal outlets Before Disinfection | Before Disinfection | Cutibacterium_acnes | 痤疮丙酸杆菌 |  | 0.1271 | 1 | Cutibacterium | - | 74 | 95 | 5.93 | 6.27 | 93 | 98 | 92 | 73 | 97 | 94 | G+ | 1.6576 | 1.7526 | 1 | 1 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_marcusii | 马氏副球菌 |  | 0.2014 | 1.01 | Paracoccus | 副球菌属 | 61 | 659 | 1.19 | 6 | 247 | 1273 | 152 | 38 | 785 | 406 | G- | 2.0847 | 10.5127 | 1 | 0.99 | id¦55983350¦BAC¦R_3491635¦ | id¦10340487¦BAC¦S_2846803¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_salipaludis | 盐沼副球菌 |  | 0.1597 | 1.01 | Paracoccus | 副球菌属 | 27 | 659 | 0.7 | 6 | 144 | 1273 | 89 | 17 | 785 | 406 | G- | 1.2294 | 10.5127 | 0.99 | 1 | id¦93777267¦BAC¦R_0130146¦ | id¦76184229¦BAC¦S_7881470¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_chinensis | 中华副球菌 |  | 0.1465 | 1 | Paracoccus | 副球菌属 | 34 | 659 | 0.63 | 6 | 131 | 1273 | 81 | 21 | 785 | 406 | G- | 1.1117 | 10.5127 | 1 | 0.95 | id¦69158942¦BAC¦R_6058228¦ | id¦41562470¦BAC¦S_5448745¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_haeundaensis | 海云台副球菌 |  | 0.141 | 1.01 | Paracoccus | 副球菌属 | 21 | 659 | 0.61 | 6 | 142 | 1273 | 88 | 13 | 785 | 406 | G- | 1.0699 | 10.5127 | 0.99 | 0.99 | id¦47592400¦BAC¦R_8989754¦ | id¦94751509¦BAC¦S_7160571¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_sediminis | 沉积物副球菌 |  | 0.0846 | 1 | Paracoccus | 副球菌属 | 19 | 659 | 0.37 | 6 | 76 | 1273 | 47 | 12 | 785 | 406 | G- | 0.6428 | 10.5127 | 1 | 0.97 | id¦79034600¦BAC¦R_0608582¦ | id¦41244491¦BAC¦S_1739464¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_sphaerophysae | 苦马豆副球菌 |  | 0.062 | 1 | Paracoccus | 副球菌属 | 19 | 659 | 0.27 | 6 | 51 | 1273 | 31 | 12 | 785 | 406 | G- | 0.4687 | 10.5127 | 1 | 1 | id¦75714865¦BAC¦R_7943103¦ | id¦90637328¦BAC¦S_9453463¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_zhejiangensis | 浙江副球菌 |  | 0.0427 | 1 | Paracoccus | 副球菌属 | 13 | 659 | 0.19 | 6 | 42 | 1273 | 26 | 8 | 785 | 406 | G- | 0.325 | 10.5127 | 1 | 0.98 | id¦11169936¦BAC¦R_8712340¦ | id¦66732144¦BAC¦S_6284677¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_marinus | 滨海副球菌 |  | 0.0391 | 1 | Paracoccus | 副球菌属 | 15 | 659 | 0.17 | 6 | 30 | 1273 | 19 | 9 | 785 | 406 | G- | 0.2962 | 10.5127 | 1 | 0.99 | id¦56010813¦BAC¦R_9036646¦ | id¦64668586¦BAC¦S_1905079¦
D | Terminal outlets Before Disinfection | Before Disinfection | Acinetobacter_baumannii | 鲍曼不动杆菌 |  | 2.31 | 1.02 | Acinetobacter | 不动杆菌属 | 1365 | 4994 | 3.1 | 5.9 | 2887 | 5372 | 1360 | 643 | 2530 | 2352 | G- | 16.2698 | 30.9345 | 1 | 1 | id¦96500901¦BAC¦R_6463796¦ | id¦50407874¦BAC¦S_9440389¦
D | Terminal outlets Before Disinfection | Before Disinfection | Acinetobacter_pittii | 皮特不动杆菌 |  | 0.8909 | 1.01 | Acinetobacter | 不动杆菌属 | 361 | 4994 | 1.44 | 5.9 | 1310 | 5372 | 617 | 170 | 2530 | 2352 | G- | 7.5353 | 30.9345 | 1 | 0.99 | id¦96937021¦BAC¦R_0931565¦ | id¦03436274¦BAC¦S_1720317¦
D | Terminal outlets Before Disinfection | Before Disinfection | Acinetobacter_nosocomialis | 医院不动杆菌 |  | 0.1652 | 1.01 | Acinetobacter | 不动杆菌属 | 24 | 4994 | 0.27 | 5.9 | 238 | 5372 | 112 | 11 | 2530 | 2352 | G- | 1.3924 | 30.9345 | 0.99 | 0.98 | id¦95183210¦BAC¦R_4912748¦ | id¦32029616¦BAC¦S_0651356¦
D | Terminal outlets Before Disinfection | Before Disinfection | Pseudomonas_aeruginosa | 铜绿假单胞菌 |  | 3.12 | 1.02 | Pseudomonas | 假单胞菌属 | 393 | 8056 | 4.25 | 5.75 | 7164 | 9399 | 3374 | 185 | 4427 | 3794 | G- | 22.3041 | 30.1662 | 0.99 | 0.97 | id¦39866963¦BAC¦R_2319190¦ | id¦01116727¦BAC¦S_0393240¦
G | Terminal outlets Before Disinfection | Before Disinfection | Pseudoxanthomonas_mexicana | 墨西哥假黄单胞菌 |  | 0.0547 | 1 | Pseudoxanthomonas | 假黄单胞菌属 | 46 | 80 | 3.25 | 5.65 | 73 | 124 | 72 | 45 | 122 | 79 | G- | 0.9085 | 1.578 | 1 | 0.99 | id¦68305743¦BAC¦R_3306448¦ | id¦99651352¦BAC¦S_9158862¦
R253 | Terminal outlets After Disinfection | After Disinfection | Corynebacterium_accolens | 拥挤棒杆菌 |  | 0.1314 | 1.02 | Corynebacterium | 棒杆菌属 | 23 | 389 | 1.12 | 5.13 | 101 | 477 | 84 | 19 | 396 | 323 | G+ | 1.7768 | 8.1205 | 0.98 | 1 | id¦75200432¦BAC¦R_6551730¦ | id¦02988577¦BAC¦S_8255987¦
R253 | Terminal outlets After Disinfection | After Disinfection | Corynebacterium_kefirresidentii | 棒杆菌* |  | 0.0716 | 1 | Corynebacterium | 棒杆菌属 | 15 | 389 | 0.46 | 5.13 | 44 | 477 | 37 | 12 | 396 | 323 | G+ | 0.7283 | 8.1205 | 1 | 1 | id¦95009171¦BAC¦R_3817316¦ | id¦54970579¦BAC¦S_3204552¦
B | Terminal outlets Before Disinfection | Before Disinfection | Afipia_broomeae | 布氏阿菲波菌 |  | 0.5955 | 1.07 | Afipia | 阿菲波菌属 | 252 | 322 | 3.67 | 4.71 | 929 | 1156 | 1269 | 344 | 1579 | 440 | G- | 12.0643 | 15.4687 | 0.94 | 0.89 | id¦29031645¦BAC¦R_6061149¦ | id¦62543115¦BAC¦S_7555421¦
E | Terminal outlets Before Disinfection | Before Disinfection | Afipia_broomeae | 布氏阿菲波菌 |  | 3.21 | 1.54 | Afipia | 阿菲波菌属 | 1719 | 2146 | 3.24 | 4.38 | 7236 | 9439 | 2384 | 566 | 3110 | 707 | G- | 22.6655 | 30.6338 | 0.66 | 0.88 | id¦29031645¦BAC¦R_6061149¦ | id¦62543115¦BAC¦S_7555421¦
E | Terminal outlets Before Disinfection | Before Disinfection | Afipia_birgiae | 伯氏阿菲波菌 |  | 0.4272 | 1.37 | Afipia | 阿菲波菌属 | 46 | 2146 | 0.33 | 4.38 | 748 | 9439 | 246 | 15 | 3110 | 707 | G- | 2.324 | 30.6338 | 0.73 | 0.95 | id¦74295584¦BAC¦R_1169345¦ | id¦31763722¦BAC¦S_6041812¦
E | Terminal outlets Before Disinfection | Before Disinfection | Afipia_felis | 猫阿菲波菌 |  | 0.2722 | 1.18 | Afipia | 阿菲波菌属 | 28 | 2146 | 0.31 | 4.38 | 520 | 9439 | 171 | 9 | 3110 | 707 | G- | 2.1746 | 30.6338 | 0.85 | 0.98 | id¦59561000¦BAC¦R_2839961¦ | id¦52327751¦BAC¦S_3068862¦
E | Terminal outlets Before Disinfection | Before Disinfection | Afipia_clevelandensis | 克利夫兰阿菲波菌 |  | 0.4131 | 1.15 | Afipia | 阿菲波菌属 | 54 | 2146 | 0.27 | 4.38 | 508 | 9439 | 167 | 18 | 3110 | 707 | G- | 1.9046 | 30.6338 | 0.87 | 0.99 | id¦86374797¦BAC¦R_9956430¦ | id¦84408437¦BAC¦S_4696916¦
E | Terminal outlets Before Disinfection | Before Disinfection | Afipia_massiliensis | 马赛阿菲波菌 |  | 0.3431 | 1.14 | Afipia | 阿菲波菌属 | 14 | 2146 | 0.22 | 4.38 | 427 | 9439 | 141 | 5 | 3110 | 707 | G- | 1.5651 | 30.6338 | 0.88 | 1 | id¦94041456¦BAC¦R_1598466¦ | id¦32470304¦BAC¦S_5018894¦
B | Terminal outlets Before Disinfection | Before Disinfection | Cutibacterium_acnes | 痤疮丙酸杆菌 |  | 0.5972 | 1.01 | Cutibacterium | - | 411 | 539 | 3.97 | 4.36 | 529 | 576 | 723 | 561 | 787 | 736 | G+ | 13.0548 | 14.3433 | 0.99 | 0.99 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
B | Terminal outlets Before Disinfection | Before Disinfection | [Propionibacterium]_humerusii | 丙酸杆菌* |  | 0.0279 | 1 | Cutibacterium | - | 16 | 539 | 0.14 | 4.36 | 18 | 576 | 25 | 22 | 787 | 736 | G+ | 0.4655 | 14.3433 | 1 | 0.82 | id¦86513342¦BAC¦R_5508967¦ | id¦75777035¦BAC¦S_4250800¦
G | Terminal outlets Before Disinfection | Before Disinfection | Acinetobacter_schindleri | 逊德勒不动杆菌 |  | 0.015 | 1 | Acinetobacter | 不动杆菌属 | 12 | 65 | 0.88 | 4.02 | 15 | 79 | 15 | 12 | 78 | 64 | G- | 0.2466 | 1.1231 | 1 | 0.94 | id¦14444543¦BAC¦R_2628493¦ | id¦04946454¦BAC¦S_3813180¦
D | Terminal outlets Before Disinfection | Before Disinfection | Haemophilus_parainfluenzae | 副流感嗜血杆菌 |  | 0.5382 | 1.01 | Haemophilus | 嗜血杆菌属 | 512 | 1292 | 1.62 | 3.73 | 780 | 1714 | 367 | 241 | 807 | 609 | G- | 8.504 | 19.5797 | 1 | 0.99 | id¦52743183¦BAC¦R_1826836¦ | id¦77177367¦BAC¦S_3784721¦
D | Terminal outlets Before Disinfection | Before Disinfection | Haemophilus_influenzae | 流感嗜血杆菌 |  | 0.4019 | 1.02 | Haemophilus | 嗜血杆菌属 | 35 | 1292 | 0.72 | 3.73 | 305 | 1714 | 144 | 16 | 807 | 609 | G- | 3.7774 | 19.5797 | 0.99 | 1 | id¦06903796¦BAC¦R_8884219¦ | id¦18099526¦BAC¦S_8633350¦
D | Terminal outlets Before Disinfection | Before Disinfection | Haemophilus_parahaemolyticus | 副溶血嗜血杆菌 |  | 0.3297 | 1.01 | Haemophilus | 嗜血杆菌属 | 138 | 1292 | 0.55 | 3.73 | 261 | 1714 | 123 | 65 | 807 | 609 | G- | 2.9053 | 19.5797 | 0.99 | 1 | id¦49365410¦BAC¦R_0657172¦ | id¦00930571¦BAC¦S_6950772¦
D | Terminal outlets Before Disinfection | Before Disinfection | Haemophilus_haemolyticus | 溶血嗜血杆菌 |  | 0.1862 | 1 | Haemophilus | 嗜血杆菌属 | 36 | 1292 | 0.54 | 3.73 | 229 | 1714 | 108 | 17 | 807 | 609 | G- | 2.8419 | 19.5797 | 1 | 0.98 | id¦74289045¦BAC¦R_9023543¦ | id¦09638923¦BAC¦S_0445775¦
D | Terminal outlets Before Disinfection | Before Disinfection | Haemophilus_paraphrohaemolyticus | 副溶血嗜沫嗜血杆菌 |  | 0.0602 | 1 | Haemophilus | 嗜血杆菌属 | 11 | 1292 | 0.1 | 3.73 | 50 | 1714 | 24 | 5 | 807 | 609 | G- | 0.5506 | 19.5797 | 1 | 0.95 | id¦45725370¦BAC¦R_3628403¦ | id¦97858433¦BAC¦S_2507581¦
R249 | Terminal outlets After Disinfection | After Disinfection | Corynebacterium_sanguinis | 血液棒杆菌 |  | 0.1211 | 1 | Corynebacterium | 棒杆菌属 | 18 | 405 | 0.73 | 3.56 | 98 | 495 | 60 | 11 | 305 | 250 | G+ | 1.2748 | 6.2323 | 1 | 0.98 | id¦88001552¦BAC¦R_4816725¦ | id¦23891647¦BAC¦S_5037140¦
R249 | Terminal outlets After Disinfection | After Disinfection | Corynebacterium_appendicis | 阑尾炎棒杆菌 |  | 0.0729 | 1 | Corynebacterium | 棒杆菌属 | 29 | 405 | 0.31 | 3.56 | 40 | 495 | 25 | 18 | 305 | 250 | G+ | 0.5486 | 6.2323 | 1 | 0.93 | id¦15236184¦BAC¦R_5754930¦ | id¦90480661¦BAC¦S_7194876¦
R249 | Terminal outlets After Disinfection | After Disinfection | Corynebacterium_striatum | 纹带棒杆菌 |  | 0.0348 | 1 | Corynebacterium | 棒杆菌属 | 19 | 405 | 0.16 | 3.56 | 26 | 495 | 16 | 12 | 305 | 250 | G+ | 0.2873 | 6.2323 | 1 | 1 | id¦68846109¦BAC¦R_4445394¦ | id¦42438174¦BAC¦S_8998241¦
R249 | Terminal outlets After Disinfection | After Disinfection | Corynebacterium_doosanense | 斗山棒杆菌 |  | 0.0319 | 1 | Corynebacterium | 棒杆菌属 | 15 | 405 | 0.14 | 3.56 | 21 | 495 | 13 | 9 | 305 | 250 | G+ | 0.2424 | 6.2323 | 1 | 0.98 | id¦11293268¦BAC¦R_2541649¦ | id¦27154330¦BAC¦S_8464624¦
R253 | Terminal outlets After Disinfection | After Disinfection | Herbaspirillum_frisingense | 弗赖森草螺菌 |  | 0.2505 | 1 | Herbaspirillum | 草螺菌属 | 188 | 436 | 2.21 | 3.35 | 456 | 699 | 379 | 156 | 580 | 362 | G- | 3.5025 | 5.2952 | 1 | 0.98 | id¦62011200¦BAC¦R_8507783¦ | id¦95314841¦BAC¦S_9462331¦
R249 | Terminal outlets After Disinfection | After Disinfection | Streptococcus_salivarius | 唾液链球菌 |  | 0.0966 | 1.03 | Streptococcus | 链球菌属 | 56 | 317 | 0.99 | 3.24 | 136 | 397 | 84 | 35 | 245 | 196 | G+ | 1.7327 | 5.6721 | 0.98 | 0.97 | id¦41857058¦BAC¦R_8555328¦ | id¦87078916¦BAC¦S_8037111¦
R249 | Terminal outlets After Disinfection | After Disinfection | Streptococcus_parasanguinis | 副血链球菌 |  | 0.0311 | 1.02 | Streptococcus | 链球菌属 | 19 | 317 | 0.27 | 3.24 | 32 | 397 | 20 | 12 | 245 | 196 | G+ | 0.4775 | 5.6721 | 0.98 | 1 | id¦77315528¦BAC¦R_4550179¦ | id¦39376444¦BAC¦S_8063262¦
R253 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_epidermidis | 表皮葡萄球菌 |  | 0.2338 | 1.01 | Staphylococcus | 葡萄球菌属 | 197 | 313 | 2.13 | 3.23 | 227 | 332 | 188 | 164 | 276 | 260 | G+ | 3.3742 | 5.1129 | 0.99 | 0.97 | id¦15608884¦BAC¦R_9898902¦ | id¦81948656¦BAC¦S_6145183¦
R253 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_hominis | 人葡萄球菌 |  | 0.056 | 1 | Staphylococcus | 葡萄球菌属 | 36 | 313 | 0.47 | 3.23 | 42 | 332 | 35 | 30 | 276 | 260 | G+ | 0.7449 | 5.1129 | 1 | 0.99 | id¦58178458¦BAC¦R_6499156¦ | id¦01588904¦BAC¦S_1607535¦
G | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_hominis | 人葡萄球菌 |  | 0.03 | 1 | Staphylococcus | 葡萄球菌属 | 17 | 38 | 1.6 | 3.05 | 21 | 43 | 21 | 17 | 42 | 37 | G+ | 0.4459 | 0.8512 | 1 | 0.93 | id¦14432767¦BAC¦R_8607399¦ | id¦01588904¦BAC¦S_1607535¦
R252 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_epidermidis | 表皮葡萄球菌 |  | 0.0692 | 1.02 | Staphylococcus | 葡萄球菌属 | 48 | 136 | 0.98 | 2.98 | 56 | 156 | 25 | 21 | 70 | 61 | G+ | 0.4484 | 1.3638 | 0.98 | 0.87 | id¦15608884¦BAC¦R_9898902¦ | id¦81948656¦BAC¦S_6145183¦
R252 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_capitis | 头葡萄球菌 |  | 0.0523 | 1 | Staphylococcus | 葡萄球菌属 | 24 | 136 | 0.69 | 2.98 | 35 | 156 | 16 | 11 | 70 | 61 | G+ | 0.3172 | 1.3638 | 1 | 0.99 | id¦91254114¦BAC¦R_4675524¦ | id¦78222658¦BAC¦S_6642837¦
R252 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_hominis | 人葡萄球菌 |  | 0.0318 | 1.04 | Staphylococcus | 葡萄球菌属 | 25 | 136 | 0.61 | 2.98 | 29 | 156 | 13 | 11 | 70 | 61 | G+ | 0.2779 | 1.3638 | 0.96 | 0.78 | id¦21131355¦BAC¦R_7789825¦ | id¦01588904¦BAC¦S_1607535¦
R252 | Terminal outlets After Disinfection | After Disinfection | Staphylococcus_saccharolyticus | 解糖葡萄球菌 |  | 0.0288 | 1 | Staphylococcus | 葡萄球菌属 | 14 | 136 | 0.33 | 2.98 | 16 | 156 | 7 | 6 | 70 | 61 | G+ | 0.1506 | 1.3638 | 1 | 0.98 | id¦14772592¦BAC¦R_5924387¦ | id¦45821870¦BAC¦S_1523047¦
R249 | Terminal outlets After Disinfection | After Disinfection | Blastococcus_saxobsidens | 居岩芽生球菌 |  | 0.2238 | 1.02 | Blastococcus | 芽生球菌属 | 122 | 200 | 1.89 | 2.89 | 438 | 713 | 270 | 75 | 440 | 123 | G+ | 3.3095 | 5.0555 | 0.98 | 0.98 | id¦75982189¦BAC¦R_3496942¦ | id¦28838149¦BAC¦S_5089509¦
R249 | Terminal outlets After Disinfection | After Disinfection | Blastococcus_colisei | 体育馆芽生球菌 |  | 0.0735 | 1 | Blastococcus | 芽生球菌属 | 11 | 200 | 0.32 | 2.89 | 95 | 713 | 59 | 7 | 440 | 123 | G+ | 0.5677 | 5.0555 | 1 | 0.95 | id¦50386987¦BAC¦R_5905650¦ | id¦53859069¦BAC¦S_6367070¦
D | Terminal outlets Before Disinfection | Before Disinfection | Rothia_mucilaginosa | 黏液罗氏菌 |  | 0.9397 | 1 | Rothia | 罗氏菌属 | 846 | 1168 | 2.23 | 2.85 | 1140 | 1480 | 537 | 398 | 697 | 550 | G+ | 11.71 | 14.9635 | 1 | 1 | id¦25827608¦BAC¦R_0635913¦ | id¦64873621¦BAC¦S_0860975¦
D | Terminal outlets Before Disinfection | Before Disinfection | Rothia_dentocariosa | 龋齿罗氏菌 |  | 0.2197 | 1.01 | Rothia | 罗氏菌属 | 187 | 1168 | 0.46 | 2.85 | 247 | 1480 | 116 | 88 | 697 | 550 | G+ | 2.4086 | 14.9635 | 1 | 1 | id¦73897219¦BAC¦R_2444668¦ | id¦50670100¦BAC¦S_5532997¦
D | Terminal outlets Before Disinfection | Before Disinfection | Rothia_aeria | 空间罗氏菌 |  | 0.0957 | 1 | Rothia | 罗氏菌属 | 61 | 1168 | 0.16 | 2.85 | 90 | 1480 | 42 | 29 | 697 | 550 | G+ | 0.8164 | 14.9635 | 1 | 0.97 | id¦00465950¦BAC¦R_4598757¦ | id¦83993854¦BAC¦S_3471784¦
R249 | Terminal outlets After Disinfection | After Disinfection | Micrococcus_luteus | 藤黄微球菌 |  | 0.1587 | 1.01 | Micrococcus | 微球菌属 | 11 | 307 | 1.08 | 2.83 | 157 | 396 | 97 | 7 | 244 | 189 | G+ | 1.892 | 4.9581 | 0.99 | 1 | id¦09080425¦BAC¦R_8971320¦ | id¦80537523¦BAC¦S_1440446¦
D | Terminal outlets Before Disinfection | Before Disinfection | Veillonella_parvula | 小韦荣球菌 |  | 0.3832 | 1 | Veillonella | 韦荣球菌属 | 94 | 1121 | 0.84 | 2.83 | 410 | 1334 | 193 | 44 | 628 | 528 | G- | 4.4323 | 14.8271 | 1 | 0.99 | id¦45550624¦BAC¦R_8006035¦ | id¦39606067¦BAC¦S_3266782¦
D | Terminal outlets Before Disinfection | Before Disinfection | Veillonella_atypica | 非典型韦荣球菌 |  | 0.3611 | 1 | Veillonella | 韦荣球菌属 | 172 | 1121 | 0.74 | 2.83 | 340 | 1334 | 160 | 81 | 628 | 528 | G- | 3.8901 | 14.8271 | 1 | 1 | id¦74095271¦BAC¦R_2656030¦ | id¦89315361¦BAC¦S_5539862¦
D | Terminal outlets Before Disinfection | Before Disinfection | Veillonella_dispar | 殊异韦荣球菌 |  | 0.2728 | 1 | Veillonella | 韦荣球菌属 | 82 | 1121 | 0.63 | 2.83 | 298 | 1334 | 140 | 39 | 628 | 528 | G- | 3.3152 | 14.8271 | 1 | 1 | id¦75949508¦BAC¦R_6483552¦ | id¦13834056¦BAC¦S_3119423¦
R249 | Terminal outlets After Disinfection | After Disinfection | Micrococcus_flavus | 黄色微球菌 |  | 0.0648 | 1 | Micrococcus | 微球菌属 | 25 | 307 | 0.28 | 2.83 | 40 | 396 | 25 | 15 | 244 | 189 | G+ | 0.4912 | 4.9581 | 1 | 1 | id¦81978827¦BAC¦R_7199605¦ | id¦49178414¦BAC¦S_3609329¦
D | Terminal outlets Before Disinfection | Before Disinfection | Veillonella_tobetsuensis | 当别町韦荣球菌 |  | 0.153 | 1 | Veillonella | 韦荣球菌属 | 45 | 1121 | 0.25 | 2.83 | 117 | 1334 | 55 | 21 | 628 | 528 | G- | 1.2894 | 14.8271 | 1 | 1 | id¦51046910¦BAC¦R_3465163¦ | id¦44318116¦BAC¦S_3146416¦
D | Terminal outlets Before Disinfection | Before Disinfection | Veillonella_infantium | 婴儿韦荣球菌 |  | 0.1555 | 1 | Veillonella | 韦荣球菌属 | 13 | 1121 | 0.17 | 2.83 | 77 | 1334 | 36 | 6 | 628 | 528 | G- | 0.8971 | 14.8271 | 1 | 0.99 | id¦82205676¦BAC¦R_1278353¦ | id¦11802572¦BAC¦S_7879875¦
D | Terminal outlets Before Disinfection | Before Disinfection | Veillonella_rogosae | 罗氏韦荣球菌 |  | 0.1479 | 1 | Veillonella | 韦荣球菌属 | 29 | 1121 | 0.16 | 2.83 | 79 | 1334 | 37 | 14 | 628 | 528 | G- | 0.8506 | 14.8271 | 1 | 1 | id¦54857280¦BAC¦R_6866107¦ | id¦02529736¦BAC¦S_5350885¦
R249 | Terminal outlets After Disinfection | After Disinfection | Micrococcus_lylae | 里拉微球菌 |  | 0.0352 | 1 | Micrococcus | 微球菌属 | 14 | 307 | 0.15 | 2.83 | 23 | 396 | 14 | 9 | 244 | 189 | G+ | 0.2646 | 4.9581 | 1 | 0.97 | id¦45830710¦BAC¦R_7007996¦ | id¦69017005¦BAC¦S_8992946¦
R249 | Terminal outlets After Disinfection | After Disinfection | Micrococcus_terreus | 土微球菌 |  | 0.033 | 1 | Micrococcus | 微球菌属 | 16 | 307 | 0.14 | 2.83 | 25 | 396 | 15 | 10 | 244 | 189 | G+ | 0.2497 | 4.9581 | 1 | 0.99 | id¦58203890¦BAC¦R_2437942¦ | id¦66191775¦BAC¦S_0069957¦
G | Terminal outlets Before Disinfection | Before Disinfection | Hydrotalea_flava | - |  | 0.0347 | 1 | Hydrotalea | - | 23 | 23 | 2.72 | 2.77 | 27 | 28 | 27 | 23 | 28 | 23 | G- | 0.7597 | 0.7748 | 1 | 0.84 | id¦35807908¦BAC¦R_2583170¦ | id¦94051955¦BAC¦S_8621411¦
D | Terminal outlets Before Disinfection | Before Disinfection | Corynebacterium_striatum | 纹带棒杆菌 |  | 1.35 | 1.02 | Corynebacterium | 棒杆菌属 | 903 | 1497 | 1.94 | 2.77 | 1209 | 1670 | 569 | 425 | 787 | 705 | G+ | 10.202 | 14.5147 | 0.99 | 1 | id¦68846109¦BAC¦R_4445394¦ | id¦42438174¦BAC¦S_8998241¦
D | Terminal outlets Before Disinfection | Before Disinfection | Corynebacterium_argentoratense | 银堡棒杆菌 |  | 0.0966 | 1 | Corynebacterium | 棒杆菌属 | 45 | 1497 | 0.11 | 2.77 | 48 | 1670 | 23 | 21 | 787 | 705 | G+ | 0.5563 | 14.5147 | 1 | 1 | id¦47562656¦BAC¦R_2251856¦ | id¦60608609¦BAC¦S_0718061¦
D | Terminal outlets Before Disinfection | Before Disinfection | Corynebacterium_matruchotii | 马氏棒杆菌 |  | 0.0359 | 1 | Corynebacterium | 棒杆菌属 | 35 | 1497 | 0.06 | 2.77 | 39 | 1670 | 18 | 16 | 787 | 705 | G+ | 0.3097 | 14.5147 | 1 | 0.99 | id¦12132327¦BAC¦R_9396860¦ | id¦97708468¦BAC¦S_4004107¦
D | Terminal outlets Before Disinfection | Before Disinfection | Corynebacterium_durum | 坚硬棒杆菌 |  | 0.051 | 1 | Corynebacterium | 棒杆菌属 | 34 | 1497 | 0.06 | 2.77 | 40 | 1670 | 19 | 16 | 787 | 705 | G+ | 0.3356 | 14.5147 | 1 | 0.99 | id¦04722516¦BAC¦R_3389727¦ | id¦45240673¦BAC¦S_9398249¦
D | Terminal outlets Before Disinfection | Before Disinfection | Corynebacterium_resistens | 抗性棒杆菌 |  | 0.0361 | 1 | Corynebacterium | 棒杆菌属 | 11 | 1497 | 0.04 | 2.77 | 23 | 1670 | 11 | 5 | 787 | 705 | G+ | 0.2082 | 14.5147 | 1 | 0.85 | id¦38019705¦BAC¦R_9560497¦ | id¦09795786¦BAC¦S_8619337¦
R253 | Terminal outlets After Disinfection | After Disinfection | Pseudomonas_alcaligenes | 产碱假单胞菌 |  | 0.0371 | 1 | Pseudomonas | 假单胞菌属 | 32 | 427 | 0.4 | 2.76 | 77 | 603 | 64 | 27 | 501 | 355 | G- | 0.6373 | 4.3706 | 1 | 0.97 | id¦01730270¦BAC¦R_4673067¦ | id¦73667852¦BAC¦S_3353884¦
R253 | Terminal outlets After Disinfection | After Disinfection | Pseudomonas_stutzeri | 斯氏假单胞菌 |  | 0.0242 | 1.01 | Pseudomonas | 假单胞菌属 | 22 | 427 | 0.23 | 2.76 | 39 | 603 | 32 | 18 | 501 | 355 | G- | 0.3585 | 4.3706 | 0.99 | 1 | id¦63805686¦BAC¦R_6394282¦ | id¦06200357¦BAC¦S_4557053¦
E | Terminal outlets Before Disinfection | Before Disinfection | Rhodopseudomonas_palustris | 沼泽红假单胞菌 |  | 0.5964 | 1.18 | Rhodopseudomonas | 红假单胞菌属 | 161 | 321 | 1.7 | 2.6 | 3857 | 5731 | 1271 | 53 | 1889 | 106 | G- | 11.9191 | 18.1599 | 0.85 | 1 | id¦16003013¦BAC¦R_1702738¦ | id¦76656959¦BAC¦S_4555826¦
E | Terminal outlets Before Disinfection | Before Disinfection | Rhodopseudomonas_pseudopalustris | 假沼泽红假单胞菌 |  | 0.4257 | 1.23 | Rhodopseudomonas | 红假单胞菌属 | 42 | 321 | 0.3 | 2.6 | 676 | 5731 | 223 | 14 | 1889 | 106 | G- | 2.1124 | 18.1599 | 0.81 | 0.98 | id¦20404293¦BAC¦R_1548206¦ | id¦48600315¦BAC¦S_7252798¦
E | Terminal outlets Before Disinfection | Before Disinfection | Rhodopseudomonas_faecalis | 粪红假单胞菌 |  | 0.3935 | 1.2 | Rhodopseudomonas | 红假单胞菌属 | 23 | 321 | 0.27 | 2.6 | 467 | 5731 | 154 | 8 | 1889 | 106 | G- | 1.8912 | 18.1599 | 0.84 | 1 | id¦03779062¦BAC¦R_1152900¦ | id¦04592315¦BAC¦S_5231768¦
R252 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_johnsonii | 约翰逊不动杆菌 |  | 0.0397 | 1.02 | Acinetobacter | 不动杆菌属 | 15 | 147 | 1.13 | 2.59 | 76 | 187 | 34 | 7 | 84 | 66 | G- | 0.5182 | 1.186 | 0.98 | 0.94 | id¦04639657¦BAC¦R_9974391¦ | id¦65226855¦BAC¦S_5801168¦
R252 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_ursingii | 乌尔辛不动杆菌 |  | 0.016 | 1.04 | Acinetobacter | 不动杆菌属 | 23 | 147 | 0.34 | 2.59 | 25 | 187 | 11 | 10 | 84 | 66 | G- | 0.1548 | 1.186 | 0.96 | 0.94 | id¦56135610¦BAC¦R_5924471¦ | id¦58318179¦BAC¦S_7032917¦
R248 | Terminal outlets After Disinfection | After Disinfection | Prevotella_histicola | 栖组织普雷沃菌 |  | 0.0254 | 1 | Prevotella | 普雷沃菌属 | 25 | 35 | 1.6 | 2.48 | 26 | 41 | 36 | 35 | 57 | 49 | G- | 0.593 | 0.923 | 1 | 0.99 | id¦29346480¦BAC¦R_1672806¦ | id¦54869476¦BAC¦S_7805381¦
R249 | Terminal outlets After Disinfection | After Disinfection | Nocardioides_dokdonensis | 独岛类诺卡菌 |  | 0.0438 | 1.03 | Nocardioides | 类诺卡菌属 | 12 | 149 | 0.2 | 2.45 | 49 | 611 | 30 | 7 | 377 | 92 | G+ | 0.3452 | 4.29 | 0.97 | 0.9 | id¦41742986¦BAC¦R_4654580¦ | id¦22754902¦BAC¦S_3170494¦
R249 | Terminal outlets After Disinfection | After Disinfection | Sphingomonas_echinoides | 多刺形鞘氨醇单胞菌 |  | 0.0696 | 1 | Sphingomonas | 鞘氨醇单胞菌属 | 47 | 121 | 0.3 | 2.42 | 71 | 509 | 44 | 29 | 314 | 75 | G- | 0.5237 | 4.2333 | 1 | 0.97 | id¦49048856¦BAC¦R_8015597¦ | id¦25279112¦BAC¦S_2088235¦
B | Terminal outlets Before Disinfection | Before Disinfection | Rhodopseudomonas_palustris | 沼泽红假单胞菌 |  | 0.0695 | 1.05 | Rhodopseudomonas | 红假单胞菌属 | 16 | 37 | 1.57 | 2.38 | 402 | 596 | 549 | 22 | 814 | 51 | G- | 5.1504 | 7.8217 | 0.95 | 0.98 | id¦16003013¦BAC¦R_1702738¦ | id¦76656959¦BAC¦S_4555826¦
R253 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_johnsonii | 约翰逊不动杆菌 |  | 0.0627 | 1 | Acinetobacter | 不动杆菌属 | 18 | 275 | 0.67 | 2.34 | 97 | 315 | 81 | 15 | 262 | 228 | G- | 1.0618 | 3.6972 | 1 | 1 | id¦90978368¦BAC¦R_1422457¦ | id¦65226855¦BAC¦S_5801168¦
R253 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_junii | 琼氏不动杆菌 |  | 0.0283 | 1 | Acinetobacter | 不动杆菌属 | 12 | 275 | 0.23 | 2.34 | 29 | 315 | 24 | 10 | 262 | 228 | G- | 0.3611 | 3.6972 | 1 | 0.94 | id¦83436215¦BAC¦R_6577620¦ | id¦62389735¦BAC¦S_6702589¦
R253 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_indicus | 斑头雁不动杆菌 |  | 0.0166 | 1 | Acinetobacter | 不动杆菌属 | 18 | 275 | 0.16 | 2.34 | 20 | 315 | 17 | 15 | 262 | 228 | G- | 0.2586 | 3.6972 | 1 | 0.99 | id¦82588051¦BAC¦R_8062221¦ | id¦48299549¦BAC¦S_2449578¦
R253 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_ursingii | 乌尔辛不动杆菌 |  | 0.0161 | 1 | Acinetobacter | 不动杆菌属 | 16 | 275 | 0.15 | 2.34 | 20 | 315 | 17 | 13 | 262 | 228 | G- | 0.2336 | 3.6972 | 1 | 0.94 | id¦19873420¦BAC¦R_8497763¦ | id¦58318179¦BAC¦S_7032917¦
R253 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_haemolyticus | 溶血不动杆菌 |  | 0.0161 | 1 | Acinetobacter | 不动杆菌属 | 11 | 275 | 0.14 | 2.34 | 19 | 315 | 16 | 9 | 262 | 228 | G- | 0.2248 | 3.6972 | 1 | 0.98 | id¦75829460¦BAC¦R_8778402¦ | id¦78616786¦BAC¦S_1216457¦
R253 | Terminal outlets After Disinfection | After Disinfection | Moraxella_osloensis | 奥斯陆莫拉菌 |  | 0.1413 | 1 | Moraxella | 莫拉菌属 | 181 | 186 | 2.19 | 2.24 | 203 | 207 | 169 | 150 | 172 | 154 | G- | 3.4616 | 3.5371 | 1 | 0.98 | id¦87618811¦BAC¦R_6389213¦ | id¦03018125¦BAC¦S_5034603¦
R252 | Terminal outlets After Disinfection | After Disinfection | Lawsonella_clevelandensis | - |  | 0.1853 | 1.02 | Lawsonella | - | 68 | 68 | 2.15 | 2.15 | 70 | 70 | 31 | 30 | 31 | 30 | G+ | 0.984 | 0.984 | 0.98 | 0.99 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
R253 | Terminal outlets After Disinfection | After Disinfection | Azonexus_fungiphilus | - |  | 0.2705 | 1 | Azonexus | - | 203 | 225 | 2.05 | 2.11 | 282 | 290 | 234 | 169 | 241 | 187 | G- | 3.2421 | 3.3416 | 1 | 1 | id¦36745070¦BAC¦R_4411413¦ | id¦23124500¦BAC¦S_7558470¦
R253 | Terminal outlets After Disinfection | After Disinfection | Delftia_tsuruhatensis | 鶴羽田代尔夫特菌 |  | 0.1191 | 1 | Delftia | 代尔夫特菌属 | 17 | 450 | 1.02 | 2.1 | 257 | 558 | 213 | 14 | 463 | 374 | G- | 1.6155 | 3.3249 | 1 | 1 | id¦07980385¦BAC¦R_4686900¦ | id¦77043306¦BAC¦S_7892112¦
R253 | Terminal outlets After Disinfection | After Disinfection | Delftia_acidovorans | 食酸代尔夫特菌 |  | 0.0751 | 1 | Delftia | 代尔夫特菌属 | 12 | 450 | 0.62 | 2.1 | 174 | 558 | 144 | 10 | 463 | 374 | G- | 0.9746 | 3.3249 | 1 | 0.99 | id¦10178606¦BAC¦R_7672023¦ | id¦25585541¦BAC¦S_9184453¦
D | Terminal outlets Before Disinfection | Before Disinfection | Methylobacterium_radiotolerans | 耐辐射甲基杆菌 |  | 0.9109 | 1.01 | Methylobacterium | 甲基杆菌属 | 69 | 2867 | 1.14 | 2.05 | 1948 | 3292 | 918 | 32 | 1551 | 1350 | G- | 5.9603 | 10.7361 | 1 | 0.99 | id¦19922506¦BAC¦R_4489281¦ | id¦93955112¦BAC¦S_7202747¦
D | Terminal outlets Before Disinfection | Before Disinfection | Methylobacterium_organophilum | 嗜有机甲基杆菌 |  | 0.6203 | 1 | Methylobacterium | 甲基杆菌属 | 29 | 2867 | 0.68 | 2.05 | 1025 | 3292 | 483 | 14 | 1551 | 1350 | G- | 3.5754 | 10.7361 | 1 | 1 | id¦85062053¦BAC¦R_5564383¦ | id¦07352082¦BAC¦S_8926867¦
D | Terminal outlets Before Disinfection | Before Disinfection | Methylobacterium_phyllostachyos | 刚竹甲基杆菌 |  | 0.0275 | 1.01 | Methylobacterium | 甲基杆菌属 | 11 | 2867 | 0.03 | 2.05 | 41 | 3292 | 19 | 5 | 1551 | 1350 | G- | 0.1605 | 10.7361 | 0.99 | 0.86 | id¦63145925¦BAC¦R_4220014¦ | id¦55512134¦BAC¦S_2312477¦
R249 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_junii | 琼氏不动杆菌 |  | 0.0645 | 1.01 | Acinetobacter | 不动杆菌属 | 67 | 366 | 0.44 | 2 | 86 | 407 | 53 | 41 | 251 | 226 | G- | 0.7693 | 3.4943 | 0.99 | 0.93 | id¦02713093¦BAC¦R_0113532¦ | id¦62389735¦BAC¦S_6702589¦
R249 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_indicus | 斑头雁不动杆菌 |  | 0.0399 | 1.03 | Acinetobacter | 不动杆菌属 | 28 | 366 | 0.26 | 2 | 45 | 407 | 28 | 17 | 251 | 226 | G- | 0.4532 | 3.4943 | 0.97 | 1 | id¦15520790¦BAC¦R_6452097¦ | id¦48299549¦BAC¦S_2449578¦
R249 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_ursingii | 乌尔辛不动杆菌 |  | 0.0268 | 1 | Acinetobacter | 不动杆菌属 | 38 | 366 | 0.22 | 2 | 43 | 407 | 27 | 23 | 251 | 226 | G- | 0.3771 | 3.4943 | 1 | 0.97 | id¦20897856¦BAC¦R_8590167¦ | id¦58318179¦BAC¦S_7032917¦
R249 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_nosocomialis | 医院不动杆菌 |  | 0.0375 | 1 | Acinetobacter | 不动杆菌属 | 24 | 366 | 0.21 | 2 | 49 | 407 | 30 | 15 | 251 | 226 | G- | 0.3754 | 3.4943 | 1 | 0.95 | id¦95183210¦BAC¦R_4912748¦ | id¦32029616¦BAC¦S_0651356¦
R249 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_baumannii | 鲍曼不动杆菌 |  | 0.0205 | 1.05 | Acinetobacter | 不动杆菌属 | 13 | 366 | 0.13 | 2 | 32 | 407 | 20 | 8 | 251 | 226 | G- | 0.2361 | 3.4943 | 0.96 | 0.94 | id¦96500901¦BAC¦R_6463796¦ | id¦50407874¦BAC¦S_9440389¦
R249 | Terminal outlets After Disinfection | After Disinfection | Acinetobacter_guillouiae | 吉洛不动杆菌 |  | 0.0157 | 1 | Acinetobacter | 不动杆菌属 | 18 | 366 | 0.09 | 2 | 23 | 407 | 14 | 11 | 251 | 226 | G- | 0.1525 | 3.4943 | 1 | 0.97 | id¦17019701¦BAC¦R_4174826¦ | id¦21540812¦BAC¦S_4100554¦
R253 | Terminal outlets After Disinfection | After Disinfection | Bacillus_thermoamylovorans | 热噬淀粉芽胞杆菌 |  | 0.1583 | 1.01 | Bacillus | 芽胞杆菌属 | 34 | 258 | 1.27 | 1.97 | 194 | 301 | 161 | 28 | 250 | 214 | G+ | 2.0054 | 3.125 | 0.99 | 1 | id¦74271046¦BAC¦R_0019897¦ | id¦28389882¦BAC¦S_7361258¦
R253 | Terminal outlets After Disinfection | After Disinfection | Bacillus_coagulans | 凝结芽胞杆菌 |  | 0.0292 | 1 | Bacillus | 芽胞杆菌属 | 23 | 258 | 0.24 | 1.97 | 31 | 301 | 26 | 19 | 250 | 214 | G+ | 0.3822 | 3.125 | 1 | 1 | id¦12483334¦BAC¦R_4337935¦ | id¦73577487¦BAC¦S_0270116¦
G | Terminal outlets Before Disinfection | Before Disinfection | Lawsonella_clevelandensis | - |  | 0.0438 | 1 | Lawsonella | - | 17 | 17 | 1.89 | 1.89 | 17 | 17 | 17 | 17 | 17 | 17 | G+ | 0.5271 | 0.5271 | 1 | 1 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
D | Terminal outlets Before Disinfection | Before Disinfection | Hydrotalea_flava | - |  | 0.8903 | 1.01 | Hydrotalea | - | 641 | 654 | 1.82 | 1.84 | 710 | 726 | 334 | 302 | 342 | 308 | G- | 9.5365 | 9.652 | 0.99 | 1 | id¦35807908¦BAC¦R_2583170¦ | id¦94051955¦BAC¦S_8621411¦
D | Terminal outlets Before Disinfection | Before Disinfection | Klebsiella_pneumoniae | 肺炎克雷伯菌 |  | 0.8836 | 1 | Klebsiella | 克雷伯菌属 | 401 | 1657 | 1.18 | 1.81 | 1476 | 2326 | 695 | 189 | 1096 | 780 | G- | 6.1706 | 9.5048 | 1 | 0.99 | id¦18267057¦BAC¦R_8047500¦ | id¦31759641¦BAC¦S_6419515¦
D | Terminal outlets Before Disinfection | Before Disinfection | Klebsiella_variicola | 异栖克雷伯菌 |  | 0.1614 | 1.01 | Klebsiella | 克雷伯菌属 | 12 | 1657 | 0.23 | 1.81 | 320 | 2326 | 151 | 6 | 1096 | 780 | G- | 1.1995 | 9.5048 | 0.99 | 0.97 | id¦48065169¦BAC¦R_1867028¦ | id¦61803738¦BAC¦S_4381350¦
D | Terminal outlets Before Disinfection | Before Disinfection | Klebsiella_quasipneumoniae | 类肺炎克雷伯菌 |  | 0.1391 | 1 | Klebsiella | 克雷伯菌属 | 11 | 1657 | 0.2 | 1.81 | 271 | 2326 | 128 | 5 | 1096 | 780 | G- | 1.0582 | 9.5048 | 1 | 0.99 | id¦37472663¦BAC¦R_6251677¦ | id¦85668339¦BAC¦S_8999614¦
D | Terminal outlets Before Disinfection | Before Disinfection | Klebsiella_aerogenes | 产气克雷伯菌 |  | 0.0512 | 1 | Klebsiella | 克雷伯菌属 | 37 | 1657 | 0.08 | 1.81 | 95 | 2326 | 45 | 17 | 1096 | 780 | G- | 0.4002 | 9.5048 | 1 | 0.98 | id¦17378320¦BAC¦R_1698403¦ | id¦84678871¦BAC¦S_1394539¦
R249 | Terminal outlets After Disinfection | After Disinfection | Kocuria_palustris | 沼泽库克菌 |  | 0.0756 | 1 | Kocuria | 库克菌属 | 54 | 280 | 0.42 | 1.8 | 68 | 362 | 42 | 33 | 223 | 173 | G+ | 0.7313 | 3.1515 | 1 | 1 | id¦63956593¦BAC¦R_8176251¦ | id¦65461644¦BAC¦S_9118994¦
R249 | Terminal outlets After Disinfection | After Disinfection | Kocuria_flava | 微黄库克菌 |  | 0.0219 | 1 | Kocuria | 库克菌属 | 16 | 280 | 0.1 | 1.8 | 22 | 362 | 14 | 10 | 223 | 173 | G+ | 0.1741 | 3.1515 | 1 | 0.87 | id¦12043851¦BAC¦R_4067208¦ | id¦19656100¦BAC¦S_5803775¦
R253 | Terminal outlets After Disinfection | After Disinfection | Klebsiella_variicola | 异栖克雷伯菌 |  | 0.1153 | 1 | Klebsiella | 克雷伯菌属 | 65 | 305 | 0.96 | 1.75 | 219 | 406 | 182 | 54 | 337 | 253 | G- | 1.5137 | 2.7691 | 1 | 1 | id¦37487445¦BAC¦R_9326049¦ | id¦61803738¦BAC¦S_4381350¦
R249 | Terminal outlets After Disinfection | After Disinfection | Pseudomonas_aeruginosa | 铜绿假单胞菌 |  | 0.1097 | 1 | Pseudomonas | 假单胞菌属 | 15 | 467 | 0.6 | 1.71 | 253 | 598 | 156 | 9 | 369 | 288 | G- | 1.0526 | 2.9888 | 1 | 0.97 | id¦61136721¦BAC¦R_7225414¦ | id¦01116727¦BAC¦S_0393240¦
R249 | Terminal outlets After Disinfection | After Disinfection | Pseudomonas_stutzeri | 斯氏假单胞菌 |  | 0.0364 | 1 | Pseudomonas | 假单胞菌属 | 32 | 467 | 0.22 | 1.71 | 59 | 598 | 36 | 20 | 369 | 288 | G- | 0.3849 | 2.9888 | 1 | 0.96 | id¦88645376¦BAC¦R_8221870¦ | id¦06200357¦BAC¦S_4557053¦
R249 | Terminal outlets After Disinfection | After Disinfection | Pseudomonas_balearica | 巴利阿里假单胞菌 |  | 0.0158 | 1 | Pseudomonas | 假单胞菌属 | 19 | 467 | 0.1 | 1.71 | 26 | 598 | 16 | 12 | 369 | 288 | G- | 0.1829 | 2.9888 | 1 | 0.94 | id¦87453710¦BAC¦R_3658689¦ | id¦76916168¦BAC¦S_9260501¦
R248 | Terminal outlets After Disinfection | After Disinfection | Moraxella_osloensis | 奥斯陆莫拉菌 |  | 0.0158 | 1 | Moraxella | 莫拉菌属 | 15 | 18 | 1.22 | 1.58 | 16 | 20 | 22 | 21 | 28 | 25 | G- | 0.4549 | 0.5861 | 1 | 0.32 | id¦08363753¦BAC¦R_3858713¦ | id¦03018125¦BAC¦S_5034603¦
R253 | Terminal outlets After Disinfection | After Disinfection | Paraburkholderia_tropica | 热带副伯克霍尔德菌 |  | 0.1296 | 1 | Paraburkholderia | 副伯克霍尔德菌属 | 95 | 363 | 0.92 | 1.51 | 310 | 481 | 257 | 79 | 399 | 301 | G- | 1.4502 | 2.3893 | 1 | 0.99 | id¦18032835¦BAC¦R_5444542¦ | id¦86892980¦BAC¦S_1168221¦
R252 | Terminal outlets After Disinfection | After Disinfection | Rhizobium_pusense | 普萨根瘤菌 |  | 0.0097 | 1 | Rhizobium | 根瘤菌属 | 11 | 35 | 0.18 | 1.5 | 21 | 184 | 9 | 5 | 82 | 16 | G- | 0.0816 | 0.688 | 1 | 0.72 | id¦28530440¦BAC¦R_0335379¦ | id¦54701733¦BAC¦S_2580134¦
R252 | Terminal outlets After Disinfection | After Disinfection | Rhizobium_subbaraonis | 苏巴拉奥氏根瘤菌 |  | 0.0122 | 1.01 | Rhizobium | 根瘤菌属 | 13 | 35 | 0.14 | 1.5 | 19 | 184 | 8 | 6 | 82 | 16 | G- | 0.0646 | 0.688 | 0.99 | 0.49 | id¦97894377¦BAC¦R_5749987¦ | id¦20998273¦BAC¦S_6466354¦
D | Terminal outlets Before Disinfection | Before Disinfection | Porphyromonas_somerae | 索氏卟啉单胞菌 |  | 0.7002 | 1 | Porphyromonas | 卟啉单胞菌属 | 296 | 595 | 0.78 | 1.49 | 406 | 767 | 191 | 139 | 361 | 280 | G- | 4.1004 | 7.7976 | 1 | 1 | id¦96851740¦BAC¦R_0204517¦ | id¦47795490¦BAC¦S_6105005¦
D | Terminal outlets Before Disinfection | Before Disinfection | Porphyromonas_gingivalis | 牙龈卟啉单胞菌 |  | 0.193 | 1 | Porphyromonas | 卟啉单胞菌属 | 72 | 595 | 0.3 | 1.49 | 164 | 767 | 77 | 34 | 361 | 280 | G- | 1.5556 | 7.7976 | 1 | 0.98 | id¦13159583¦BAC¦R_9155681¦ | id¦39045523¦BAC¦S_0383628¦
D | Terminal outlets Before Disinfection | Before Disinfection | Porphyromonas_endodontalis | 牙髓卟啉单胞菌 |  | 0.2272 | 1 | Porphyromonas | 卟啉单胞菌属 | 85 | 595 | 0.25 | 1.49 | 118 | 767 | 56 | 40 | 361 | 280 | G- | 1.316 | 7.7976 | 1 | 0.96 | id¦71739134¦BAC¦R_3772870¦ | id¦21478217¦BAC¦S_1175637¦
D | Terminal outlets Before Disinfection | Before Disinfection | Porphyromonas_catoniae | 卡托氏卟啉单胞菌 |  | 0.0515 | 1.09 | Porphyromonas | 卟啉单胞菌属 | 25 | 595 | 0.08 | 1.49 | 37 | 767 | 17 | 12 | 361 | 280 | G- | 0.4152 | 7.7976 | 0.92 | 0.91 | id¦49328033¦BAC¦R_9878601¦ | id¦69286950¦BAC¦S_6213056¦
R249 | Terminal outlets After Disinfection | After Disinfection | Lawsonella_clevelandensis | - |  | 0.339 | 1.02 | Lawsonella | - | 128 | 128 | 1.48 | 1.48 | 134 | 134 | 83 | 79 | 83 | 79 | G+ | 2.5972 | 2.5972 | 0.99 | 0.99 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
R248 | Terminal outlets After Disinfection | After Disinfection | Lawsonella_clevelandensis | - |  | 0.0324 | 1 | Lawsonella | - | 12 | 12 | 1.41 | 1.41 | 12 | 12 | 17 | 17 | 17 | 17 | G+ | 0.5244 | 0.5244 | 1 | 1 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
D | Terminal outlets Before Disinfection | Before Disinfection | Gemella_haemolysans | 溶血孪生球菌 |  | 0.4212 | 1 | Gemella | 孪生球菌属 | 167 | 353 | 0.81 | 1.4 | 339 | 576 | 160 | 79 | 271 | 166 | G+ | 4.2438 | 7.362 | 1 | 1 | id¦34286850¦BAC¦R_8980988¦ | id¦31233011¦BAC¦S_0664854¦
D | Terminal outlets Before Disinfection | Before Disinfection | Gemella_sanguinis | 血孪生球菌 |  | 0.2262 | 1 | Gemella | 孪生球菌属 | 98 | 353 | 0.37 | 1.4 | 150 | 576 | 71 | 46 | 271 | 166 | G+ | 1.9663 | 7.362 | 1 | 0.99 | id¦84200092¦BAC¦R_7738674¦ | id¦69707973¦BAC¦S_8295401¦
D | Terminal outlets Before Disinfection | Before Disinfection | Gemella_morbillorum | 麻疹孪生球菌 |  | 0.1517 | 1 | Gemella | 孪生球菌属 | 62 | 353 | 0.21 | 1.4 | 83 | 576 | 39 | 29 | 271 | 166 | G+ | 1.0985 | 7.362 | 1 | 0.99 | id¦64982882¦BAC¦R_6597626¦ | id¦29377160¦BAC¦S_2697317¦
D | Terminal outlets Before Disinfection | Before Disinfection | Stenotrophomonas_maltophilia | 嗜麦芽窄食单胞菌 |  | 0.5926 | 1 | Stenotrophomonas | 窄食单胞菌属 | 461 | 628 | 1.22 | 1.35 | 1339 | 1476 | 631 | 217 | 695 | 296 | G- | 6.3982 | 7.108 | 1 | 0.99 | id¦55851721¦BAC¦R_2396079¦ | id¦75406125¦BAC¦S_6497236¦
R249 | Terminal outlets After Disinfection | After Disinfection | Serinicoccus_profundi | 深海丝氨酸球菌 |  | 0.2816 | 1 | Serinicoccus | 丝氨酸球菌属 | 166 | 199 | 1.21 | 1.34 | 239 | 265 | 147 | 102 | 163 | 123 | G+ | 2.1204 | 2.3482 | 1 | 0.99 | id¦43464208¦BAC¦R_0602118¦ | id¦07067620¦BAC¦S_2017242¦
R253 | Terminal outlets After Disinfection | After Disinfection | Kocuria_palustris | 沼泽库克菌 |  | 0.123 | 1 | Kocuria | 库克菌属 | 110 | 129 | 1.13 | 1.33 | 124 | 148 | 103 | 91 | 123 | 107 | G+ | 1.7955 | 2.1051 | 1 | 0.98 | id¦63956593¦BAC¦R_8176251¦ | id¦65461644¦BAC¦S_9118994¦
R253 | Terminal outlets After Disinfection | After Disinfection | Rhizobium_pusense | 普萨根瘤菌 |  | 0.0529 | 1 | Rhizobium | 根瘤菌属 | 62 | 106 | 0.47 | 1.32 | 103 | 296 | 86 | 51 | 246 | 88 | G- | 0.7367 | 2.0891 | 1 | 1 | id¦43196479¦BAC¦R_7772076¦ | id¦54701733¦BAC¦S_2580134¦
R253 | Terminal outlets After Disinfection | After Disinfection | Rhizobium_subbaraonis | 苏巴拉奥氏根瘤菌 |  | 0.011 | 1.02 | Rhizobium | 根瘤菌属 | 15 | 106 | 0.07 | 1.32 | 18 | 296 | 15 | 12 | 246 | 88 | G- | 0.1136 | 2.0891 | 0.98 | 0.2 | id¦97894377¦BAC¦R_5749987¦ | id¦20998273¦BAC¦S_6466354¦
D | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_aureus | 金黄色葡萄球菌 |  | 0.3952 | 1 | Staphylococcus | 葡萄球菌属 | 236 | 591 | 0.56 | 1.16 | 387 | 714 | 182 | 111 | 336 | 278 | G+ | 2.9289 | 6.061 | 1 | 0.99 | id¦10808207¦BAC¦R_3968458¦ | id¦57618172¦BAC¦S_1289868¦
D | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_pasteuri | 巴斯德葡萄球菌 |  | 0.1763 | 1 | Staphylococcus | 葡萄球菌属 | 25 | 591 | 0.2 | 1.16 | 88 | 714 | 41 | 12 | 336 | 278 | G+ | 1.0455 | 6.061 | 1 | 0.98 | id¦29869662¦BAC¦R_8225373¦ | id¦48079179¦BAC¦S_7914094¦
D | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_epidermidis | 表皮葡萄球菌 |  | 0.1459 | 1 | Staphylococcus | 葡萄球菌属 | 93 | 591 | 0.17 | 1.16 | 107 | 714 | 50 | 44 | 336 | 278 | G+ | 0.9022 | 6.061 | 1 | 0.98 | id¦15608884¦BAC¦R_9898902¦ | id¦81948656¦BAC¦S_6145183¦
D | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_haemolyticus | 溶血葡萄球菌 |  | 0.0485 | 1 | Staphylococcus | 葡萄球菌属 | 37 | 591 | 0.07 | 1.16 | 44 | 714 | 21 | 17 | 336 | 278 | G+ | 0.3839 | 6.061 | 1 | 0.98 | id¦33823453¦BAC¦R_4061613¦ | id¦21767703¦BAC¦S_6480655¦
D | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_capitis | 头葡萄球菌 |  | 0.0299 | 1 | Staphylococcus | 葡萄球菌属 | 19 | 591 | 0.04 | 1.16 | 24 | 714 | 11 | 9 | 336 | 278 | G+ | 0.229 | 6.061 | 1 | 0.99 | id¦91254114¦BAC¦R_4675524¦ | id¦78222658¦BAC¦S_6642837¦
D | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_pettenkoferi | 佩滕科夫葡萄球菌 |  | 0.021 | 1 | Staphylococcus | 葡萄球菌属 | 11 | 591 | 0.03 | 1.16 | 15 | 714 | 7 | 5 | 336 | 278 | G+ | 0.1392 | 6.061 | 1 | 0.98 | id¦39979974¦BAC¦R_3584980¦ | id¦43498178¦BAC¦S_8828073¦
D | Terminal outlets Before Disinfection | Before Disinfection | Actinomyces_graevenitzii | 格雷文尼放线菌 |  | 0.3223 | 1 | Actinomyces | 放线菌属 | 191 | 487 | 0.52 | 1.13 | 241 | 631 | 114 | 90 | 297 | 229 | G+ | 2.7231 | 5.9518 | 1 | 1 | id¦96213277¦BAC¦R_5766226¦ | id¦89962810¦BAC¦S_3814609¦
D | Terminal outlets Before Disinfection | Before Disinfection | Actinomyces_bouchesdurhonensis | 放线菌* |  | 0.1364 | 1 | Actinomyces | 放线菌属 | 42 | 487 | 0.15 | 1.13 | 76 | 631 | 36 | 20 | 297 | 229 | G+ | 0.7905 | 5.9518 | 1 | 0.98 | id¦32846600¦BAC¦R_0049453¦ | id¦76533092¦BAC¦S_6158761¦
D | Terminal outlets Before Disinfection | Before Disinfection | Actinomyces_oris | 口腔放线菌 |  | 0.0499 | 1 | Actinomyces | 放线菌属 | 18 | 487 | 0.14 | 1.13 | 95 | 631 | 45 | 8 | 297 | 229 | G+ | 0.7353 | 5.9518 | 1 | 0.93 | id¦03688343¦BAC¦R_5678316¦ | id¦19392096¦BAC¦S_9396489¦
D | Terminal outlets Before Disinfection | Before Disinfection | Actinomyces_dentalis | 牙齿放线菌 |  | 0.0465 | 1 | Actinomyces | 放线菌属 | 34 | 487 | 0.05 | 1.13 | 40 | 631 | 19 | 16 | 297 | 229 | G+ | 0.2668 | 5.9518 | 1 | 0.97 | id¦69977362¦BAC¦R_7180295¦ | id¦22407282¦BAC¦S_8743862¦
D | Terminal outlets Before Disinfection | Before Disinfection | Actinomyces_israelii | 衣氏放线菌 |  | 0.0282 | 1 | Actinomyces | 放线菌属 | 16 | 487 | 0.03 | 1.13 | 29 | 631 | 14 | 8 | 297 | 229 | G+ | 0.1697 | 5.9518 | 1 | 0.94 | id¦00798238¦BAC¦R_7369347¦ | id¦96850026¦BAC¦S_4372465¦
R252 | Terminal outlets After Disinfection | After Disinfection | Rothia_dentocariosa | 龋齿罗氏菌 |  | 0.0285 | 1.08 | Rothia | 罗氏菌属 | 30 | 48 | 0.68 | 1.12 | 35 | 56 | 16 | 13 | 25 | 21 | G+ | 0.3129 | 0.5119 | 0.92 | 0.88 | id¦98894376¦BAC¦R_7036055¦ | id¦50670100¦BAC¦S_5532997¦
D | Terminal outlets Before Disinfection | Before Disinfection | Fusobacterium_periodonticum | 牙周梭杆菌 |  | 0.2079 | 1.01 | Fusobacterium | 梭杆菌属 | 137 | 492 | 0.42 | 1.08 | 224 | 590 | 106 | 65 | 278 | 232 | G- | 2.2001 | 5.6464 | 0.99 | 1 | id¦30455421¦BAC¦R_6458467¦ | id¦91968406¦BAC¦S_2908796¦
D | Terminal outlets Before Disinfection | Before Disinfection | Fusobacterium_nucleatum | 具核梭杆菌 |  | 0.1331 | 1 | Fusobacterium | 梭杆菌属 | 98 | 492 | 0.42 | 1.08 | 232 | 590 | 109 | 46 | 278 | 232 | G- | 2.1788 | 5.6464 | 1 | 0.98 | id¦11770108¦BAC¦R_2928731¦ | id¦77964578¦BAC¦S_3772641¦
D | Terminal outlets Before Disinfection | Before Disinfection | Fusobacterium_mortiferum | 死亡梭杆菌 |  | 0.0812 | 1 | Fusobacterium | 梭杆菌属 | 52 | 492 | 0.11 | 1.08 | 66 | 590 | 31 | 24 | 278 | 232 | G- | 0.5721 | 5.6464 | 1 | 0.99 | id¦82305470¦BAC¦R_4284234¦ | id¦63535057¦BAC¦S_7301506¦
R253 | Terminal outlets After Disinfection | After Disinfection | Lawsonella_clevelandensis | - |  | 0.1598 | 1 | Lawsonella | - | 58 | 58 | 1.07 | 1.07 | 65 | 65 | 54 | 48 | 54 | 48 | G+ | 1.6961 | 1.6961 | 1 | 0.99 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
R249 | Terminal outlets After Disinfection | After Disinfection | Rothia_mucilaginosa | 黏液罗氏菌 |  | 0.0951 | 1.01 | Rothia | 罗氏菌属 | 93 | 109 | 0.86 | 1.01 | 112 | 134 | 69 | 57 | 83 | 67 | G+ | 1.5055 | 1.7659 | 1 | 1 | id¦53027511¦BAC¦R_0150123¦ | id¦64873621¦BAC¦S_0860975¦
R249 | Terminal outlets After Disinfection | After Disinfection | Prevotella_histicola | 栖组织普雷沃菌 |  | 0.0764 | 1.01 | Prevotella | 普雷沃菌属 | 64 | 150 | 0.47 | 1.01 | 80 | 177 | 49 | 39 | 109 | 93 | G- | 0.8264 | 1.7724 | 0.99 | 0.98 | id¦33427979¦BAC¦R_9519864¦ | id¦54869476¦BAC¦S_7805381¦
R252 | Terminal outlets After Disinfection | After Disinfection | Moraxella_osloensis | 奥斯陆莫拉菌 |  | 0.0414 | 1 | Moraxella | 莫拉菌属 | 36 | 38 | 0.98 | 1 | 48 | 49 | 21 | 16 | 22 | 17 | G- | 0.4492 | 0.459 | 1 | 0.97 | id¦19374739¦BAC¦R_3281678¦ | id¦03018125¦BAC¦S_5034603¦
R248 | Terminal outlets After Disinfection | After Disinfection | Ralstonia_pickettii | 皮氏罗尔斯顿菌 |  | 0.0106 | 1 | Ralstonia | 罗尔斯顿菌属 | 16 | 22 | 0.78 | 0.99 | 22 | 28 | 31 | 22 | 39 | 31 | G- | 0.2917 | 0.3693 | 1 | 0.99 | id¦53230913¦BAC¦R_4512424¦ | id¦99940213¦BAC¦S_3917488¦
R249 | Terminal outlets After Disinfection | After Disinfection | Tepidimonas_fonticaldi | - |  | 0.1235 | 1 | Tepidimonas | - | 74 | 113 | 0.66 | 0.96 | 113 | 158 | 70 | 46 | 97 | 70 | G- | 1.1602 | 1.6757 | 1 | 0.99 | id¦36824863¦BAC¦R_2266445¦ | id¦23800547¦BAC¦S_5125954¦
D | Terminal outlets Before Disinfection | Before Disinfection | Afipia_broomeae | 布氏阿菲波菌 |  | 0.5113 | 1.07 | Afipia | 阿菲波菌属 | 219 | 293 | 0.68 | 0.93 | 800 | 1051 | 377 | 103 | 495 | 138 | G- | 3.5818 | 4.865 | 0.94 | 0.89 | id¦29031645¦BAC¦R_6061149¦ | id¦62543115¦BAC¦S_7555421¦
R249 | Terminal outlets After Disinfection | After Disinfection | Moraxella_osloensis | 奥斯陆莫拉菌 |  | 0.0973 | 1 | Moraxella | 莫拉菌属 | 115 | 126 | 0.8 | 0.9 | 135 | 147 | 83 | 71 | 91 | 78 | G- | 1.3955 | 1.5742 | 1 | 0.98 | id¦78445804¦BAC¦R_1006151¦ | id¦03018125¦BAC¦S_5034603¦
R248 | Terminal outlets After Disinfection | After Disinfection | Acidovorax_temperans | 温和食酸菌 |  | 0.0111 | 1 | Acidovorax | 食酸菌属 | 11 | 16 | 0.72 | 0.9 | 18 | 23 | 25 | 15 | 32 | 22 | G- | 0.2691 | 0.3355 | 1 | 1 | id¦02810628¦BAC¦R_8344044¦ | id¦27147656¦BAC¦S_4831994¦
R249 | Terminal outlets After Disinfection | After Disinfection | Rubellimicrobium_mesophilum | - |  | 0.1085 | 1.02 | Rubellimicrobium | - | 27 | 75 | 0.48 | 0.89 | 134 | 241 | 83 | 17 | 149 | 46 | G- | 0.8397 | 1.5605 | 0.98 | 0.99 | id¦42298572¦BAC¦R_4684524¦ | id¦96258607¦BAC¦S_0970590¦
R249 | Terminal outlets After Disinfection | After Disinfection | Rubellimicrobium_roseum | - |  | 0.0798 | 1 | Rubellimicrobium | - | 29 | 75 | 0.34 | 0.89 | 95 | 241 | 59 | 18 | 149 | 46 | G- | 0.6037 | 1.5605 | 1 | 0.99 | id¦31784287¦BAC¦R_2800080¦ | id¦26027014¦BAC¦S_0794312¦
R253 | Terminal outlets After Disinfection | After Disinfection | Burkholderia_gladioli | 唐菖蒲伯克霍尔德菌 |  | 0.0421 | 1 | Burkholderia | 伯克霍尔德菌属 | 75 | 203 | 0.34 | 0.88 | 112 | 275 | 93 | 62 | 228 | 169 | G- | 0.5308 | 1.3892 | 1 | 1 | id¦16298152¦BAC¦R_2604589¦ | id¦99758472¦BAC¦S_0790244¦
E | Terminal outlets Before Disinfection | Before Disinfection | Rhizobium_tropici | 热带根瘤菌 |  | 0.8276 | 1.19 | Rhizobium | 根瘤菌属 | 42 | 78 | 0.57 | 0.86 | 1835 | 2578 | 605 | 14 | 850 | 26 | G- | 4.0134 | 6.0382 | 0.85 | 1 | id¦93830752¦BAC¦R_1579712¦ | id¦05558986¦BAC¦S_0060946¦
D | Terminal outlets Before Disinfection | Before Disinfection | Escherichia_coli | 大肠埃希菌 |  | 0.4748 | 1.01 | Escherichia | 埃希菌属 | 178 | 262 | 0.7 | 0.85 | 853 | 1013 | 402 | 84 | 477 | 123 | G- | 3.6963 | 4.4667 | 0.99 | 0.99 | id¦54861165¦BAC¦R_9218445¦ | id¦80633099¦BAC¦S_9077810¦
R253 | Terminal outlets After Disinfection | After Disinfection | Bifidobacterium_thermacidophilum | 高温双歧杆菌 |  | 0.0602 | 1 | Bifidobacterium | 双歧杆菌属 | 11 | 59 | 0.42 | 0.84 | 36 | 71 | 30 | 9 | 59 | 49 | G+ | 0.6693 | 1.3345 | 1 | 1 | id¦83756996¦BAC¦R_4722380¦ | id¦60159582¦BAC¦S_4661531¦
R249 | Terminal outlets After Disinfection | After Disinfection | Rhizobium_pusense | 普萨根瘤菌 |  | 0.0979 | 1.02 | Rhizobium | 根瘤菌属 | 115 | 132 | 0.59 | 0.81 | 194 | 264 | 120 | 71 | 163 | 81 | G- | 1.0306 | 1.4208 | 0.98 | 1 | id¦43196479¦BAC¦R_7772076¦ | id¦54701733¦BAC¦S_2580134¦
D | Terminal outlets Before Disinfection | Before Disinfection | Moraxella_catarrhalis | 卡他莫拉菌 |  | 0.5133 | 1.01 | Moraxella | 莫拉菌属 | 235 | 322 | 0.62 | 0.74 | 281 | 348 | 132 | 111 | 164 | 152 | G- | 3.2355 | 3.9004 | 1 | 1 | id¦31563923¦BAC¦R_7061224¦ | id¦24177236¦BAC¦S_6549566¦
D | Terminal outlets Before Disinfection | Before Disinfection | Moraxella_nonliquefaciens | 非液化莫拉菌 |  | 0.0421 | 1 | Moraxella | 莫拉菌属 | 16 | 322 | 0.06 | 0.74 | 29 | 348 | 14 | 8 | 164 | 152 | G- | 0.3117 | 3.9004 | 1 | 0.9 | id¦08890418¦BAC¦R_1495212¦ | id¦14275059¦BAC¦S_8249575¦
D | Terminal outlets Before Disinfection | Before Disinfection | Moraxella_osloensis | 奥斯陆莫拉菌 |  | 0.0143 | 1 | Moraxella | 莫拉菌属 | 18 | 322 | 0.04 | 0.74 | 21 | 348 | 10 | 8 | 164 | 152 | G- | 0.192 | 3.9004 | 1 | 0.97 | id¦25712679¦BAC¦R_7352011¦ | id¦03018125¦BAC¦S_5034603¦
B | Terminal outlets Before Disinfection | Before Disinfection | Lawsonella_clevelandensis | - |  | 0.1366 | 1 | Lawsonella | - | 51 | 51 | 0.71 | 0.71 | 54 | 54 | 74 | 70 | 74 | 70 | G+ | 2.3184 | 2.3184 | 1 | 0.99 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
R253 | Terminal outlets After Disinfection | After Disinfection | Anaerococcus_nagyae | 纳吉氏厌氧球菌 |  | 0.0517 | 1 | Anaerococcus | 厌氧球菌属 | 22 | 43 | 0.33 | 0.71 | 23 | 51 | 19 | 18 | 42 | 36 | G+ | 0.5233 | 1.1291 | 1 | 0.97 | id¦53833902¦BAC¦R_8579025¦ | id¦06526781¦BAC¦S_9279551¦
R249 | Terminal outlets After Disinfection | After Disinfection | Janibacter_indicus | 印度两面神菌 |  | 0.0657 | 1 | Janibacter | 两面神菌属 | 30 | 95 | 0.3 | 0.7 | 59 | 136 | 36 | 19 | 84 | 59 | G+ | 0.532 | 1.2248 | 1 | 0.99 | id¦12017638¦BAC¦R_0838008¦ | id¦82969607¦BAC¦S_3624440¦
R253 | Terminal outlets After Disinfection | After Disinfection | Paracoccus_sphaerophysae | 苦马豆副球菌 |  | 0.0362 | 1 | Paracoccus | 副球菌属 | 19 | 56 | 0.23 | 0.69 | 30 | 92 | 25 | 16 | 76 | 46 | G- | 0.3712 | 1.0879 | 1 | 0.85 | id¦75714865¦BAC¦R_7943103¦ | id¦90637328¦BAC¦S_9453463¦
R249 | Terminal outlets After Disinfection | After Disinfection | Rubrobacter_radiotolerans | 耐辐射红色杆菌 |  | 0.1189 | 1.02 | Rubrobacter | 红色杆菌属 | 45 | 57 | 0.53 | 0.66 | 102 | 125 | 63 | 28 | 77 | 35 | G+ | 0.9256 | 1.1618 | 0.98 | 0.96 | id¦19882729¦BAC¦R_3682145¦ | id¦02313393¦BAC¦S_8472356¦
G | Terminal outlets Before Disinfection | Before Disinfection | Moraxella_osloensis | 奥斯陆莫拉菌 |  | 0.0055 | 1 | Moraxella | 莫拉菌属 | 11 | 11 | 0.65 | 0.65 | 11 | 11 | 11 | 11 | 11 | 11 | G- | 0.1819 | 0.1819 | 1 | 0.51 | id¦78445804¦BAC¦R_1006151¦ | id¦03018125¦BAC¦S_5034603¦
R253 | Terminal outlets After Disinfection | After Disinfection | Brachybacterium_paraconglomeratum | 副凝聚小短杆菌 |  | 0.0324 | 1 | Brachybacterium | 小短杆菌属 | 29 | 66 | 0.28 | 0.62 | 41 | 87 | 34 | 24 | 72 | 55 | G+ | 0.4498 | 0.9789 | 1 | 0.89 | id¦93848825¦BAC¦R_3355705¦ | id¦49034683¦BAC¦S_4138545¦
R253 | Terminal outlets After Disinfection | After Disinfection | Brachybacterium_alimentarium | 食物小短杆菌 |  | 0.0135 | 1 | Brachybacterium | 小短杆菌属 | 11 | 66 | 0.09 | 0.62 | 14 | 87 | 12 | 9 | 72 | 55 | G+ | 0.1363 | 0.9789 | 1 | 0.97 | id¦13350663¦BAC¦R_2488667¦ | id¦71762648¦BAC¦S_1563019¦
D | Terminal outlets Before Disinfection | Before Disinfection | Proteus_mirabilis | 奇异变形杆菌 |  | 0.4538 | 1 | Proteus | 变形杆菌属 | 487 | 535 | 0.59 | 0.61 | 575 | 594 | 271 | 229 | 280 | 252 | G- | 3.0968 | 3.2054 | 1 | 1 | id¦82452372¦BAC¦R_8616126¦ | id¦53136358¦BAC¦S_0457148¦
D | Terminal outlets Before Disinfection | Before Disinfection | Capnocytophaga_leadbetteri | 利氏二氧化碳噬纤维菌 |  | 0.113 | 1 | Capnocytophaga | 二氧化碳噬纤维菌属 | 75 | 305 | 0.19 | 0.59 | 111 | 375 | 52 | 35 | 177 | 144 | G- | 0.9915 | 3.1208 | 1 | 0.97 | id¦03879819¦BAC¦R_8384942¦ | id¦03490795¦BAC¦S_2272509¦
D | Terminal outlets Before Disinfection | Before Disinfection | Capnocytophaga_sputigena | 生痰二氧化碳噬纤维菌 |  | 0.0932 | 1.01 | Capnocytophaga | 二氧化碳噬纤维菌属 | 74 | 305 | 0.18 | 0.59 | 122 | 375 | 57 | 35 | 177 | 144 | G- | 0.9272 | 3.1208 | 0.99 | 0.99 | id¦76165353¦BAC¦R_8308007¦ | id¦17122586¦BAC¦S_3046375¦
D | Terminal outlets Before Disinfection | Before Disinfection | Capnocytophaga_gingivalis | 牙龈二氧化碳噬纤维菌 |  | 0.0793 | 1 | Capnocytophaga | 二氧化碳噬纤维菌属 | 59 | 305 | 0.11 | 0.59 | 68 | 375 | 32 | 28 | 177 | 144 | G- | 0.5642 | 3.1208 | 1 | 0.98 | id¦93171430¦BAC¦R_6500067¦ | id¦31765661¦BAC¦S_2463671¦
D | Terminal outlets Before Disinfection | Before Disinfection | Capnocytophaga_ochracea | 黄褐二氧化碳噬纤维菌 |  | 0.0309 | 1 | Capnocytophaga | 二氧化碳噬纤维菌属 | 20 | 305 | 0.07 | 0.59 | 39 | 375 | 18 | 9 | 177 | 144 | G- | 0.3461 | 3.1208 | 1 | 0.95 | id¦41504610¦BAC¦R_4186643¦ | id¦92721022¦BAC¦S_3492164¦
D | Terminal outlets Before Disinfection | Before Disinfection | Capnocytophaga_granulosa | 颗粒二氧化碳噬纤维菌 |  | 0.0439 | 1.01 | Capnocytophaga | 二氧化碳噬纤维菌属 | 20 | 305 | 0.05 | 0.59 | 31 | 375 | 15 | 9 | 177 | 144 | G- | 0.2567 | 3.1208 | 0.99 | 0.97 | id¦13398160¦BAC¦R_4308313¦ | id¦51176316¦BAC¦S_3725240¦
R253 | Terminal outlets After Disinfection | After Disinfection | Xanthomonas_campestris | 野油菜黄单胞菌 |  | 0.0433 | 1 | Xanthomonas | 黄单胞菌属 | 41 | 68 | 0.34 | 0.58 | 67 | 112 | 56 | 34 | 93 | 56 | G- | 0.5381 | 0.9184 | 1 | 1 | id¦56283181¦BAC¦R_3895395¦ | id¦72428435¦BAC¦S_8827926¦
E | Terminal outlets Before Disinfection | Before Disinfection | Nitrobacter_winogradskyi | 维氏硝化杆菌 |  | 0.2418 | 1.19 | Nitrobacter | 硝化杆菌属 | 12 | 32 | 0.26 | 0.55 | 374 | 890 | 123 | 4 | 293 | 11 | G- | 1.8113 | 3.8148 | 0.84 | 1 | id¦69339683¦BAC¦R_8767828¦ | id¦40335043¦BAC¦S_6219523¦
R249 | Terminal outlets After Disinfection | After Disinfection | Cloacibacterium_normanense | - |  | 0.0948 | 1 | Cloacibacterium | - | 57 | 57 | 0.54 | 0.54 | 84 | 84 | 52 | 35 | 52 | 35 | G- | 0.9387 | 0.9387 | 1 | 0.98 | id¦08036817¦BAC¦R_0859119¦ | id¦36590735¦BAC¦S_8513847¦
D | Terminal outlets Before Disinfection | Before Disinfection | Aggregatibacter_segnis | 惰性凝聚杆菌 |  | 0.2283 | 1.01 | Aggregatibacter | 凝聚杆菌属 | 116 | 169 | 0.46 | 0.54 | 206 | 246 | 97 | 55 | 116 | 80 | G- | 2.4227 | 2.8073 | 0.99 | 0.99 | id¦64069159¦BAC¦R_9027896¦ | id¦28162889¦BAC¦S_4466289¦
R253 | Terminal outlets After Disinfection | After Disinfection | Roseomonas_gilardii | 吉氏玫瑰单胞菌 |  | 0.0675 | 1 | Roseomonas | 玫瑰单胞菌属 | 58 | 93 | 0.46 | 0.54 | 91 | 107 | 76 | 48 | 89 | 77 | G- | 0.7329 | 0.8592 | 1 | 0.99 | id¦11800630¦BAC¦R_8777683¦ | id¦84077971¦BAC¦S_8673392¦
R249 | Terminal outlets After Disinfection | After Disinfection | Bacillus_nealsonii | 尼氏芽胞杆菌 |  | 0.0237 | 1.05 | Bacillus | 芽胞杆菌属 | 27 | 115 | 0.11 | 0.53 | 30 | 133 | 19 | 17 | 82 | 71 | G+ | 0.187 | 0.93 | 0.95 | 0.95 | id¦60081949¦BAC¦R_0322781¦ | id¦70554959¦BAC¦S_7420297¦
R249 | Terminal outlets After Disinfection | After Disinfection | Bacillus_coagulans | 凝结芽胞杆菌 |  | 0.011 | 1 | Bacillus | 芽胞杆菌属 | 14 | 115 | 0.07 | 0.53 | 14 | 133 | 9 | 9 | 82 | 71 | G+ | 0.1282 | 0.93 | 1 | 0.77 | id¦12483334¦BAC¦R_4337935¦ | id¦73577487¦BAC¦S_0270116¦
R249 | Terminal outlets After Disinfection | After Disinfection | Bacillus_infantis | 婴儿芽胞杆菌 |  | 0.0109 | 1 | Bacillus | 芽胞杆菌属 | 16 | 115 | 0.06 | 0.53 | 18 | 133 | 11 | 10 | 82 | 71 | G+ | 0.1136 | 0.93 | 1 | 0.78 | id¦87210667¦BAC¦R_7704631¦ | id¦30119237¦BAC¦S_9010579¦
B | Terminal outlets Before Disinfection | Before Disinfection | Aerococcus_urinae | 尿气球菌 |  | 0.0903 | 1.14 | Aerococcus | 气球菌属 | 38 | 38 | 0.52 | 0.52 | 66 | 66 | 90 | 52 | 90 | 52 | G+ | 1.7171 | 1.7171 | 0.88 | 0.93 | id¦24449035¦BAC¦R_0941850¦ | id¦46892321¦BAC¦S_9758766¦
D | Terminal outlets Before Disinfection | Before Disinfection | Rhodopseudomonas_palustris | 沼泽红假单胞菌 |  | 0.0753 | 1.01 | Rhodopseudomonas | 红假单胞菌属 | 21 | 38 | 0.32 | 0.51 | 388 | 599 | 183 | 10 | 282 | 18 | G- | 1.6572 | 2.6571 | 0.99 | 0.99 | id¦09917136¦BAC¦R_6467305¦ | id¦76656959¦BAC¦S_4555826¦
R249 | Terminal outlets After Disinfection | After Disinfection | Brachybacterium_paraconglomeratum | 副凝聚小短杆菌 |  | 0.0463 | 1 | Brachybacterium | 小短杆菌属 | 36 | 75 | 0.25 | 0.51 | 54 | 109 | 33 | 22 | 67 | 46 | G+ | 0.44 | 0.8987 | 1 | 0.92 | id¦93848825¦BAC¦R_3355705¦ | id¦49034683¦BAC¦S_4138545¦
R249 | Terminal outlets After Disinfection | After Disinfection | Brachybacterium_alimentarium | 食物小短杆菌 |  | 0.026 | 1 | Brachybacterium | 小短杆菌属 | 21 | 75 | 0.11 | 0.51 | 27 | 109 | 17 | 13 | 67 | 46 | G+ | 0.1953 | 0.8987 | 1 | 0.99 | id¦13350663¦BAC¦R_2488667¦ | id¦71762648¦BAC¦S_1563019¦
R253 | Terminal outlets After Disinfection | After Disinfection | Chryseobacterium_taklimakanense | 塔拉玛干金黄杆菌 |  | 0.0208 | 1 | Chryseobacterium | 金黄杆菌属 | 14 | 38 | 0.21 | 0.5 | 22 | 59 | 18 | 12 | 49 | 32 | G- | 0.3303 | 0.7969 | 1 | 0.9 | id¦04756579¦BAC¦R_9160412¦ | id¦58889401¦BAC¦S_5928381¦
D | Terminal outlets Before Disinfection | Before Disinfection | Enterococcus_faecium | 屎肠球菌 |  | 0.2226 | 1 | Enterococcus | 肠球菌属 | 95 | 312 | 0.28 | 0.49 | 187 | 338 | 88 | 45 | 159 | 147 | G+ | 1.4706 | 2.552 | 1 | 0.99 | id¦84477008¦BAC¦R_2704173¦ | id¦66275801¦BAC¦S_2655548¦
D | Terminal outlets Before Disinfection | Before Disinfection | Enterococcus_faecalis | 粪肠球菌 |  | 0.0896 | 1 | Enterococcus | 肠球菌属 | 79 | 312 | 0.12 | 0.49 | 83 | 338 | 39 | 37 | 159 | 147 | G+ | 0.6035 | 2.552 | 1 | 0.99 | id¦42463634¦BAC¦R_6609679¦ | id¦63612960¦BAC¦S_5510546¦
B | Terminal outlets Before Disinfection | Before Disinfection | Caulobacter_vibrioides | 弧形柄杆菌 |  | 0.0313 | 1 | Caulobacter | 柄杆菌属 | 36 | 64 | 0.29 | 0.48 | 63 | 107 | 86 | 49 | 146 | 87 | G- | 0.9375 | 1.5617 | 1 | 1 | id¦55331277¦BAC¦R_4113112¦ | id¦03591998¦BAC¦S_6058582¦
B | Terminal outlets Before Disinfection | Before Disinfection | Sphingomonas_echinoides | 多刺形鞘氨醇单胞菌 |  | 0.0265 | 1 | Sphingomonas | 鞘氨醇单胞菌属 | 12 | 23 | 0.13 | 0.48 | 27 | 97 | 37 | 16 | 133 | 31 | G- | 0.4412 | 1.5912 | 1 | 0.97 | id¦49048856¦BAC¦R_8015597¦ | id¦25279112¦BAC¦S_2088235¦
B | Terminal outlets Before Disinfection | Before Disinfection | Caulobacter_segnis | 惰性柄杆菌 |  | 0.0189 | 1 | Caulobacter | 柄杆菌属 | 13 | 64 | 0.11 | 0.48 | 26 | 107 | 36 | 18 | 146 | 87 | G- | 0.373 | 1.5617 | 1 | 0.52 | id¦03902742¦BAC¦R_4782067¦ | id¦42807857¦BAC¦S_2392370¦
D | Terminal outlets Before Disinfection | Before Disinfection | Lactobacillus_fermentum | 发酵乳杆菌 |  | 0.0534 | 1 | Lactobacillus | 乳杆菌属 | 29 | 228 | 0.07 | 0.47 | 34 | 255 | 16 | 14 | 120 | 107 | G+ | 0.3485 | 2.4562 | 1 | 0.92 | id¦74734323¦BAC¦R_0569016¦ | id¦94082386¦BAC¦S_3464758¦
D | Terminal outlets Before Disinfection | Before Disinfection | Lactobacillus_salivarius | 唾液乳杆菌 |  | 0.0421 | 1 | Lactobacillus | 乳杆菌属 | 27 | 228 | 0.06 | 0.47 | 30 | 255 | 14 | 13 | 120 | 107 | G+ | 0.3183 | 2.4562 | 1 | 1 | id¦21342105¦BAC¦R_4116843¦ | id¦62897498¦BAC¦S_9438449¦
D | Terminal outlets Before Disinfection | Before Disinfection | Lactobacillus_rhamnosus | 鼠李糖乳杆菌 |  | 0.0175 | 1 | Lactobacillus | 乳杆菌属 | 22 | 228 | 0.03 | 0.47 | 23 | 255 | 11 | 10 | 120 | 107 | G+ | 0.1777 | 2.4562 | 1 | 0.83 | id¦33794762¦BAC¦R_6648041¦ | id¦05235599¦BAC¦S_1382226¦
D | Terminal outlets Before Disinfection | Before Disinfection | Lactobacillus_crispatus | 卷曲乳杆菌 |  | 0.019 | 1 | Lactobacillus | 乳杆菌属 | 11 | 228 | 0.03 | 0.47 | 16 | 255 | 8 | 5 | 120 | 107 | G+ | 0.1588 | 2.4562 | 1 | 0.83 | id¦82519573¦BAC¦R_0391478¦ | id¦92449702¦BAC¦S_8227188¦
D | Terminal outlets Before Disinfection | Before Disinfection | Cutibacterium_acnes | 痤疮丙酸杆菌 |  | 0.2669 | 1 | Cutibacterium | - | 166 | 255 | 0.37 | 0.46 | 230 | 275 | 108 | 78 | 130 | 120 | G+ | 1.9569 | 2.3964 | 1 | 0.97 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
B | Terminal outlets Before Disinfection | Before Disinfection | Prevotella_melaninogenica | 产黑色普雷沃菌 |  | 0.0304 | 1 | Prevotella | 普雷沃菌属 | 22 | 58 | 0.27 | 0.46 | 43 | 72 | 59 | 30 | 98 | 79 | G- | 0.876 | 1.5126 | 1 | 0.8 | id¦38256307¦BAC¦R_2212743¦ | id¦61369871¦BAC¦S_1570876¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bacteroides_fragilis | 脆弱拟杆菌 |  | 0.0687 | 1 | Bacteroides | 拟杆菌属 | 104 | 450 | 0.1 | 0.46 | 123 | 558 | 58 | 49 | 263 | 212 | G- | 0.5391 | 2.4158 | 1 | 0.99 | id¦49414417¦BAC¦R_9815848¦ | id¦67975829¦BAC¦S_4008282¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bacteroides_vulgatus | 普通拟杆菌 |  | 0.048 | 1 | Bacteroides | 拟杆菌属 | 20 | 450 | 0.07 | 0.46 | 79 | 558 | 37 | 9 | 263 | 212 | G- | 0.3603 | 2.4158 | 1 | 0.95 | id¦68502581¦BAC¦R_5683638¦ | id¦12992872¦BAC¦S_4672442¦
D | Terminal outlets Before Disinfection | Before Disinfection | [Propionibacterium]_namnetense | - |  | 0.0523 | 1 | Cutibacterium | - | 17 | 255 | 0.06 | 0.46 | 31 | 275 | 15 | 8 | 130 | 120 | G+ | 0.3003 | 2.3964 | 1 | 0.98 | id¦98833027¦BAC¦R_8182154¦ | id¦85186092¦BAC¦S_0590636¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bacteroides_heparinolyticus | 解肝素拟杆菌 |  | 0.0318 | 1 | Bacteroides | 拟杆菌属 | 26 | 450 | 0.05 | 0.46 | 42 | 558 | 20 | 12 | 263 | 212 | G- | 0.2741 | 2.4158 | 1 | 0.96 | id¦10473565¦BAC¦R_3168354¦ | id¦87180257¦BAC¦S_0181488¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bacteroides_thetaiotaomicron | 多形拟杆菌 |  | 0.0266 | 1.01 | Bacteroides | 拟杆菌属 | 49 | 450 | 0.04 | 0.46 | 63 | 558 | 30 | 23 | 263 | 212 | G- | 0.2275 | 2.4158 | 0.99 | 0.97 | id¦54979416¦BAC¦R_6757910¦ | id¦36308058¦BAC¦S_1899560¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bacteroides_cellulosilyticus | 解纤维素拟杆菌 |  | 0.0193 | 1 | Bacteroides | 拟杆菌属 | 20 | 450 | 0.03 | 0.46 | 51 | 558 | 24 | 9 | 263 | 212 | G- | 0.167 | 2.4158 | 1 | 0.98 | id¦61697193¦BAC¦R_1487616¦ | id¦27425506¦BAC¦S_1114258¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bacteroides_stercoris | 粪便拟杆菌 |  | 0.0115 | 1 | Bacteroides | 拟杆菌属 | 11 | 450 | 0.02 | 0.46 | 18 | 558 | 8 | 5 | 263 | 212 | G- | 0.1005 | 2.4158 | 1 | 0.92 | id¦84977585¦BAC¦R_0103868¦ | id¦36019499¦BAC¦S_1308436¦
R252 | Terminal outlets After Disinfection | After Disinfection | Ralstonia_pickettii | 皮氏罗尔斯顿菌 |  | 0.0172 | 1 | Ralstonia | 罗尔斯顿菌属 | 29 | 38 | 0.38 | 0.45 | 41 | 49 | 18 | 13 | 22 | 17 | G- | 0.1748 | 0.2079 | 1 | 0.99 | id¦53230913¦BAC¦R_4512424¦ | id¦99940213¦BAC¦S_3917488¦
D | Terminal outlets Before Disinfection | Before Disinfection | Granulicatella_adiacens | 毗邻颗粒链菌 |  | 0.3192 | 1.01 | Granulicatella | 颗粒链菌属 | 86 | 107 | 0.36 | 0.45 | 153 | 190 | 72 | 41 | 89 | 50 | G+ | 1.8734 | 2.3711 | 0.99 | 1 | id¦14208282¦BAC¦R_8828940¦ | id¦63289353¦BAC¦S_6129138¦
R253 | Terminal outlets After Disinfection | After Disinfection | Acidovorax_temperans | 温和食酸菌 |  | 0.0275 | 1 | Acidovorax | 食酸菌属 | 26 | 41 | 0.25 | 0.45 | 42 | 77 | 35 | 22 | 64 | 34 | G- | 0.3906 | 0.7185 | 1 | 0.96 | id¦31462359¦BAC¦R_5117359¦ | id¦27147656¦BAC¦S_4831994¦
R249 | Terminal outlets After Disinfection | After Disinfection | Mycolicibacterium_doricum | 多瑞卡分枝杆菌 |  | 0.0392 | 1 | Mycolicibacterium | - | 19 | 42 | 0.17 | 0.45 | 39 | 133 | 24 | 12 | 82 | 26 | G+ | 0.2985 | 0.7804 | 1 | 0.96 | id¦94863900¦BAC¦R_7992614¦ | id¦72870500¦BAC¦S_0880549¦
D | Terminal outlets Before Disinfection | Before Disinfection | Granulicatella_elegans | 苛养颗粒链菌 |  | 0.0843 | 1 | Granulicatella | 颗粒链菌属 | 18 | 107 | 0.09 | 0.45 | 36 | 190 | 17 | 8 | 89 | 50 | G+ | 0.4867 | 2.3711 | 1 | 0.99 | id¦95864646¦BAC¦R_4381988¦ | id¦48705058¦BAC¦S_8585361¦
D | Terminal outlets Before Disinfection | Before Disinfection | Schaalia_odontolytica | - |  | 0.1644 | 1 | Schaalia | - | 40 | 62 | 0.37 | 0.44 | 195 | 231 | 92 | 19 | 109 | 29 | G+ | 1.9185 | 2.3136 | 1 | 0.99 | id¦71186116¦BAC¦R_5097659¦ | id¦80976677¦BAC¦S_0530070¦
D | Terminal outlets Before Disinfection | Before Disinfection | Schaalia_turicensis | - |  | 0.0273 | 1 | Schaalia | - | 12 | 62 | 0.03 | 0.44 | 14 | 231 | 7 | 6 | 109 | 29 | G+ | 0.1689 | 2.3136 | 1 | 0.99 | id¦82771830¦BAC¦R_9142813¦ | id¦79984185¦BAC¦S_3121148¦
E | Terminal outlets Before Disinfection | Before Disinfection | Dyella_jiangningensis | 江宁戴氏菌 |  | 0.5395 | 1.34 | Dyella | 戴氏菌属 | 31 | 32 | 0.41 | 0.42 | 882 | 902 | 291 | 10 | 297 | 11 | G- | 2.8458 | 2.918 | 0.75 | 0.02 | id¦43066553¦BAC¦R_0044859¦ | id¦00820652¦BAC¦S_5025524¦
R249 | Terminal outlets After Disinfection | After Disinfection | Anaerococcus_nagyae | 纳吉氏厌氧球菌 |  | 0.067 | 1 | Anaerococcus | 厌氧球菌属 | 19 | 32 | 0.29 | 0.42 | 30 | 44 | 19 | 12 | 27 | 20 | G+ | 0.507 | 0.7344 | 1 | 0.93 | id¦53833902¦BAC¦R_8579025¦ | id¦06526781¦BAC¦S_9279551¦
R253 | Terminal outlets After Disinfection | After Disinfection | Pseudoxanthomonas_spadix | 褐色假黄单胞菌 |  | 0.0315 | 1 | Pseudoxanthomonas | 假黄单胞菌属 | 15 | 27 | 0.2 | 0.42 | 36 | 67 | 30 | 12 | 56 | 22 | G- | 0.32 | 0.668 | 1 | 0.98 | id¦53894863¦BAC¦R_2943111¦ | id¦89243648¦BAC¦S_0997163¦
E | Terminal outlets Before Disinfection | Before Disinfection | Aerococcus_urinae | 尿气球菌 |  | 0.4276 | 1.65 | Aerococcus | 气球菌属 | 242 | 244 | 0.41 | 0.41 | 457 | 459 | 151 | 80 | 151 | 80 | G+ | 2.8678 | 2.8844 | 0.61 | 0.87 | id¦24449035¦BAC¦R_0941850¦ | id¦46892321¦BAC¦S_9758766¦
E | Terminal outlets Before Disinfection | Before Disinfection | Tardiphaga_robiniae | - |  | 0.3491 | 1.2 | Tardiphaga | - | 45 | 45 | 0.4 | 0.4 | 1073 | 1073 | 354 | 15 | 354 | 15 | G- | 2.7864 | 2.7864 | 0.83 | 1 | id¦65343753¦BAC¦R_9749611¦ | id¦60367483¦BAC¦S_9615632¦
R253 | Terminal outlets After Disinfection | After Disinfection | Thermoanaerobacterium_thermosaccharolyticum | 热解糖热厌氧细菌 |  | 0.0452 | 1 | Thermoanaerobacterium | 热厌氧细菌属 | 12 | 12 | 0.4 | 0.4 | 43 | 43 | 36 | 10 | 36 | 10 | G+ | 0.6408 | 0.6408 | 1 | 0.98 | id¦78665014¦BAC¦R_4368679¦ | id¦10491588¦BAC¦S_0272332¦
R253 | Terminal outlets After Disinfection | After Disinfection | Aureimonas_phyllosphaerae | 叶球形金色单胞菌 |  | 0.0332 | 1.01 | Aureimonas | 金色单胞菌属 | 18 | 34 | 0.22 | 0.4 | 39 | 69 | 32 | 15 | 57 | 28 | G- | 0.3433 | 0.6265 | 0.99 | 0.95 | id¦97875737¦BAC¦R_8218194¦ | id¦48487321¦BAC¦S_4543746¦
R249 | Terminal outlets After Disinfection | After Disinfection | Candidatus_Rickettsiella_isopodorum | 立克次小体* |  | 0.0882 | 1 | Rickettsiella | 立克次小体属 | 30 | 30 | 0.38 | 0.39 | 32 | 33 | 20 | 19 | 20 | 19 | G- | 0.6633 | 0.6828 | 1 | 0.94 | id¦70249318¦BAC¦R_8108927¦ | id¦69994668¦BAC¦S_5666967¦
D | Terminal outlets Before Disinfection | Before Disinfection | Mycoplasma_salivarium | 唾液支原体 |  | 0.2801 | 1 | Mycoplasma | 支原体属 | 45 | 55 | 0.31 | 0.39 | 49 | 62 | 23 | 21 | 29 | 26 | G- | 1.6169 | 2.025 | 1 | 0.97 | id¦51973247¦BAC¦R_8549392¦ | id¦89847201¦BAC¦S_1956414¦
R249 | Terminal outlets After Disinfection | After Disinfection | Xanthomonas_campestris | 野油菜黄单胞菌 |  | 0.0447 | 1 | Xanthomonas | 黄单胞菌属 | 45 | 66 | 0.25 | 0.39 | 72 | 112 | 44 | 28 | 69 | 41 | G- | 0.4295 | 0.6801 | 1 | 1 | id¦56283181¦BAC¦R_3895395¦ | id¦72428435¦BAC¦S_8827926¦
D | Terminal outlets Before Disinfection | Before Disinfection | Leptotrichia_wadei | 韦德纤毛菌 |  | 0.1401 | 1 | Leptotrichia | 纤毛菌属 | 75 | 171 | 0.24 | 0.39 | 123 | 209 | 58 | 35 | 98 | 81 | G- | 1.2401 | 2.0618 | 1 | 0.97 | id¦05907475¦BAC¦R_3583748¦ | id¦24310541¦BAC¦S_5691087¦
R249 | Terminal outlets After Disinfection | After Disinfection | Haemophilus_parainfluenzae | 副流感嗜血杆菌 |  | 0.0147 | 1.03 | Haemophilus | 嗜血杆菌属 | 11 | 38 | 0.15 | 0.39 | 18 | 47 | 11 | 7 | 29 | 23 | G- | 0.257 | 0.6887 | 0.97 | 0.89 | id¦52743183¦BAC¦R_1826836¦ | id¦77177367¦BAC¦S_3784721¦
R252 | Terminal outlets After Disinfection | After Disinfection | Xanthomonas_campestris | 野油菜黄单胞菌 |  | 0.0233 | 1 | Xanthomonas | 黄单胞菌属 | 22 | 29 | 0.32 | 0.37 | 34 | 38 | 15 | 10 | 17 | 13 | G- | 0.1471 | 0.1675 | 1 | 0.99 | id¦56283181¦BAC¦R_3895395¦ | id¦72428435¦BAC¦S_8827926¦
R249 | Terminal outlets After Disinfection | After Disinfection | Micromonospora_globbae | 舞花姜微单胞菌 |  | 0.0398 | 1 | Micromonospora | 微单胞菌属 | 38 | 60 | 0.17 | 0.37 | 69 | 147 | 43 | 23 | 91 | 37 | G+ | 0.3002 | 0.6506 | 1 | 0.99 | id¦08234325¦BAC¦R_4249772¦ | id¦05282626¦BAC¦S_2651648¦
R249 | Terminal outlets After Disinfection | After Disinfection | Acidovorax_temperans | 温和食酸菌 |  | 0.0289 | 1 | Acidovorax | 食酸菌属 | 26 | 45 | 0.15 | 0.37 | 39 | 103 | 24 | 16 | 64 | 28 | G- | 0.2586 | 0.6439 | 1 | 0.99 | id¦02810628¦BAC¦R_8344044¦ | id¦27147656¦BAC¦S_4831994¦
E | Terminal outlets Before Disinfection | Before Disinfection | Cutibacterium_acnes | 痤疮丙酸杆菌 |  | 0.4683 | 1.01 | Cutibacterium | - | 309 | 385 | 0.32 | 0.35 | 379 | 409 | 125 | 102 | 135 | 127 | G+ | 2.256 | 2.46 | 1 | 0.97 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
R249 | Terminal outlets After Disinfection | After Disinfection | Stenotrophomonas_maltophilia | 嗜麦芽窄食单胞菌 |  | 0.0245 | 1 | Stenotrophomonas | 窄食单胞菌属 | 21 | 31 | 0.22 | 0.35 | 61 | 92 | 38 | 13 | 57 | 19 | G- | 0.393 | 0.6171 | 1 | 0.93 | id¦44145980¦BAC¦R_2199819¦ | id¦75406125¦BAC¦S_6497236¦
R252 | Terminal outlets After Disinfection | After Disinfection | Azonexus_fungiphilus | - |  | 0.0214 | 1 | Azonexus | - | 17 | 18 | 0.34 | 0.34 | 25 | 25 | 11 | 8 | 11 | 8 | G- | 0.1548 | 0.1548 | 1 | 0.97 | id¦36745070¦BAC¦R_4411413¦ | id¦23124500¦BAC¦S_7558470¦
R249 | Terminal outlets After Disinfection | After Disinfection | Pseudoxanthomonas_mexicana | 墨西哥假黄单胞菌 |  | 0.0186 | 1 | Pseudoxanthomonas | 假黄单胞菌属 | 13 | 21 | 0.13 | 0.34 | 28 | 71 | 17 | 8 | 44 | 13 | G- | 0.2194 | 0.5957 | 1 | 0.97 | id¦96443360¦BAC¦R_7173934¦ | id¦99651352¦BAC¦S_9158862¦
E | Terminal outlets Before Disinfection | Before Disinfection | Sphingomonas_echinoides | 多刺形鞘氨醇单胞菌 |  | 0.0908 | 1 | Sphingomonas | 鞘氨醇单胞菌属 | 42 | 114 | 0.05 | 0.34 | 91 | 609 | 30 | 14 | 201 | 38 | G- | 0.3586 | 2.4014 | 1 | 0.98 | id¦49048856¦BAC¦R_8015597¦ | id¦25279112¦BAC¦S_2088235¦
E | Terminal outlets Before Disinfection | Before Disinfection | Sphingomonas_leidyi | 莱氏鞘氨醇单胞菌 |  | 0.0725 | 1 | Sphingomonas | 鞘氨醇单胞菌属 | 32 | 114 | 0.04 | 0.34 | 83 | 609 | 27 | 11 | 201 | 38 | G- | 0.2856 | 2.4014 | 1 | 0.98 | id¦05939620¦BAC¦R_4014801¦ | id¦13446957¦BAC¦S_2229055¦
D | Terminal outlets Before Disinfection | Before Disinfection | Campylobacter_concisus | 简明弯曲菌 |  | 0.069 | 1 | Campylobacter | 弯曲菌属 | 67 | 126 | 0.19 | 0.33 | 85 | 155 | 40 | 32 | 73 | 59 | G- | 1.0209 | 1.746 | 1 | 1 | id¦11601658¦BAC¦R_8756155¦ | id¦09225893¦BAC¦S_6771200¦
D | Terminal outlets Before Disinfection | Before Disinfection | Campylobacter_showae | 昭和弯曲菌 |  | 0.032 | 1 | Campylobacter | 弯曲菌属 | 17 | 126 | 0.07 | 0.33 | 36 | 155 | 17 | 8 | 73 | 59 | G- | 0.3924 | 1.746 | 1 | 0.79 | id¦74387101¦BAC¦R_9902838¦ | id¦31948925¦BAC¦S_3303306¦
D | Terminal outlets Before Disinfection | Before Disinfection | Campylobacter_rectus | 直肠弯曲菌 |  | 0.0255 | 1 | Campylobacter | 弯曲菌属 | 12 | 126 | 0.04 | 0.33 | 23 | 155 | 11 | 6 | 73 | 59 | G- | 0.2106 | 1.746 | 1 | 0.95 | id¦08642637¦BAC¦R_2271458¦ | id¦51756282¦BAC¦S_3739360¦
R249 | Terminal outlets After Disinfection | After Disinfection | Atopobium_parvulum | 极小陌生菌 |  | 0.0699 | 1.02 | Atopobium | 陌生菌属 | 15 | 15 | 0.32 | 0.32 | 28 | 28 | 17 | 9 | 17 | 9 | G+ | 0.5653 | 0.5653 | 0.98 | 0.99 | id¦30051589¦BAC¦R_2978760¦ | id¦23054861¦BAC¦S_8819107¦
R249 | Terminal outlets After Disinfection | After Disinfection | Ralstonia_pickettii | 皮氏罗尔斯顿菌 |  | 0.0356 | 1 | Ralstonia | 罗尔斯顿菌属 | 57 | 80 | 0.25 | 0.32 | 77 | 100 | 47 | 35 | 62 | 49 | G- | 0.4333 | 0.5612 | 1 | 1 | id¦03468833¦BAC¦R_5245223¦ | id¦99940213¦BAC¦S_3917488¦
B | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_epidermidis | 表皮葡萄球菌 |  | 0.0176 | 1 | Staphylococcus | 葡萄球菌属 | 12 | 36 | 0.1 | 0.32 | 13 | 40 | 18 | 16 | 55 | 49 | G+ | 0.3179 | 1.0532 | 1 | 0.98 | id¦15608884¦BAC¦R_9898902¦ | id¦81948656¦BAC¦S_6145183¦
R252 | Terminal outlets After Disinfection | After Disinfection | Stenotrophomonas_maltophilia | 嗜麦芽窄食单胞菌 |  | 0.0085 | 1 | Stenotrophomonas | 窄食单胞菌属 | 11 | 12 | 0.2 | 0.31 | 21 | 30 | 9 | 5 | 13 | 5 | G- | 0.093 | 0.1406 | 1 | 0.86 | id¦55242059¦BAC¦R_6016505¦ | id¦75406125¦BAC¦S_6497236¦
R249 | Terminal outlets After Disinfection | After Disinfection | Klebsiella_pneumoniae | 肺炎克雷伯菌 |  | 0.0348 | 1 | Klebsiella | 克雷伯菌属 | 16 | 71 | 0.18 | 0.31 | 56 | 100 | 35 | 10 | 62 | 44 | G- | 0.3075 | 0.5416 | 1 | 0.97 | id¦65145872¦BAC¦R_7114571¦ | id¦31759641¦BAC¦S_6419515¦
D | Terminal outlets Before Disinfection | Before Disinfection | Burkholderia_cenocepacia | 新洋葱伯克霍尔德菌 |  | 0.0893 | 1 | Burkholderia | 伯克霍尔德菌属 | 74 | 399 | 0.12 | 0.31 | 229 | 580 | 108 | 35 | 273 | 188 | G- | 0.6257 | 1.651 | 1 | 1 | id¦81710899¦BAC¦R_2461569¦ | id¦47633230¦BAC¦S_7638737¦
D | Terminal outlets Before Disinfection | Before Disinfection | Parvimonas_micra | 微小微单胞菌 |  | 0.1701 | 1 | Parvimonas | 微单胞菌属 | 90 | 90 | 0.29 | 0.29 | 105 | 105 | 49 | 42 | 49 | 42 | G+ | 1.5199 | 1.5199 | 1 | 0.98 | id¦83329511¦BAC¦R_1722616¦ | id¦97218525¦BAC¦S_0104274¦
D | Terminal outlets Before Disinfection | Before Disinfection | Peptostreptococcus_stomatis | 口腔消化链球菌 |  | 0.2475 | 1 | Peptostreptococcus | 消化链球菌属 | 99 | 109 | 0.27 | 0.29 | 120 | 129 | 57 | 47 | 61 | 51 | G+ | 1.4296 | 1.5341 | 1 | 0.99 | id¦51404264¦BAC¦R_0009508¦ | id¦62906680¦BAC¦S_3603114¦
B | Terminal outlets Before Disinfection | Before Disinfection | Rothia_mucilaginosa | 黏液罗氏菌 |  | 0.0319 | 1 | Rothia | 罗氏菌属 | 19 | 25 | 0.24 | 0.29 | 26 | 33 | 36 | 26 | 45 | 34 | G+ | 0.7746 | 0.962 | 1 | 0.97 | id¦25827608¦BAC¦R_0635913¦ | id¦64873621¦BAC¦S_0860975¦
E | Terminal outlets Before Disinfection | Before Disinfection | Rhodoplanes_roseus | 玫瑰色红游动菌 |  | 0.0926 | 1.21 | Rhodoplanes | 红游动菌属 | 13 | 45 | 0.06 | 0.28 | 185 | 731 | 61 | 4 | 241 | 15 | G- | 0.4524 | 1.9824 | 0.83 | 0.99 | id¦84382087¦BAC¦R_8075315¦ | id¦41694820¦BAC¦S_8006908¦
B | Terminal outlets Before Disinfection | Before Disinfection | Moraxella_osloensis | 奥斯陆莫拉菌 |  | 0.0283 | 1 | Moraxella | 莫拉菌属 | 28 | 28 | 0.27 | 0.27 | 33 | 33 | 45 | 38 | 45 | 38 | G- | 0.8753 | 0.8753 | 1 | 0.98 | id¦25712679¦BAC¦R_7352011¦ | id¦03018125¦BAC¦S_5034603¦
R253 | Terminal outlets After Disinfection | After Disinfection | Thermicanus_aegyptius | - |  | 0.0423 | 1 | Thermicanus | - | 24 | 24 | 0.27 | 0.27 | 38 | 38 | 32 | 20 | 32 | 20 | G+ | 0.4314 | 0.4314 | 1 | 0.9 | id¦47245291¦BAC¦R_6414753¦ | id¦22984817¦BAC¦S_0920229¦
D | Terminal outlets Before Disinfection | Before Disinfection | Alloprevotella_tannerae | 坦纳拟普雷沃菌 |  | 0.1907 | 1 | Alloprevotella | 拟普雷沃菌属 | 91 | 109 | 0.21 | 0.27 | 121 | 157 | 57 | 43 | 74 | 51 | G- | 1.1038 | 1.4324 | 1 | 0.99 | id¦75517206¦BAC¦R_5083143¦ | id¦84040174¦BAC¦S_1579734¦
D | Terminal outlets Before Disinfection | Before Disinfection | Mogibacterium_diversum | 分生艰难杆菌 |  | 0.173 | 1.01 | Mogibacterium | 艰难杆菌属 | 50 | 83 | 0.19 | 0.27 | 78 | 111 | 37 | 24 | 52 | 39 | G+ | 1.0116 | 1.431 | 0.99 | 0.99 | id¦51862509¦BAC¦R_2709706¦ | id¦04893366¦BAC¦S_9783661¦
D | Terminal outlets Before Disinfection | Before Disinfection | Alloprevotella_rava | 灰色拟普雷沃菌 |  | 0.0554 | 1.03 | Alloprevotella | 拟普雷沃菌属 | 18 | 109 | 0.06 | 0.27 | 36 | 157 | 17 | 8 | 74 | 51 | G- | 0.3286 | 1.4324 | 0.98 | 0.97 | id¦88137567¦BAC¦R_4590377¦ | id¦35038853¦BAC¦S_5213503¦
D | Terminal outlets Before Disinfection | Before Disinfection | Mogibacterium_timidum | 怯生艰难杆菌 |  | 0.0483 | 1 | Mogibacterium | 艰难杆菌属 | 18 | 83 | 0.05 | 0.27 | 22 | 111 | 10 | 8 | 52 | 39 | G+ | 0.2787 | 1.431 | 1 | 0.97 | id¦53161046¦BAC¦R_3981408¦ | id¦52616374¦BAC¦S_0744669¦
R249 | Terminal outlets After Disinfection | After Disinfection | Brevibacterium_ihuae | 短杆菌* |  | 0.0225 | 1 | Brevibacterium | 短杆菌属 | 14 | 34 | 0.1 | 0.26 | 17 | 50 | 10 | 9 | 31 | 21 | G+ | 0.1693 | 0.4505 | 1 | 0.84 | id¦70134763¦BAC¦R_6900828¦ | id¦82281919¦BAC¦S_7989666¦
R249 | Terminal outlets After Disinfection | After Disinfection | Brevibacterium_casei | 乳酪短杆菌 |  | 0.0118 | 1 | Brevibacterium | 短杆菌属 | 11 | 34 | 0.07 | 0.26 | 15 | 50 | 9 | 7 | 31 | 21 | G+ | 0.1237 | 0.4505 | 1 | 0.99 | id¦36075030¦BAC¦R_7313027¦ | id¦50364648¦BAC¦S_0402074¦
D | Terminal outlets Before Disinfection | Before Disinfection | Lautropia_mirabilis | 奇异劳特罗普菌 |  | 0.2252 | 1 | Lautropia | 劳特罗普菌属 | 128 | 128 | 0.25 | 0.25 | 176 | 176 | 83 | 60 | 83 | 60 | G- | 1.3067 | 1.3067 | 1 | 0.99 | id¦50555833¦BAC¦R_3773357¦ | id¦48261277¦BAC¦S_8489393¦
B | Terminal outlets Before Disinfection | Before Disinfection | Enhydrobacter_aerosaccus | 气囊栖水菌 |  | 0.0441 | 1.05 | Enhydrobacter | 栖水菌属 | 50 | 50 | 0.24 | 0.24 | 77 | 77 | 105 | 68 | 105 | 68 | G- | 0.7772 | 0.7772 | 0.95 | 0.57 | id¦19544319¦BAC¦R_9865596¦ | id¦15638415¦BAC¦S_7626718¦
R249 | Terminal outlets After Disinfection | After Disinfection | Isoptericola_variabilis | 变异白蚁菌 |  | 0.0486 | 1 | Isoptericola | 白蚁菌属 | 14 | 15 | 0.22 | 0.24 | 30 | 34 | 19 | 9 | 21 | 9 | G+ | 0.3846 | 0.4163 | 1 | 0.99 | id¦54249479¦BAC¦R_5040128¦ | id¦64495660¦BAC¦S_6274438¦
B | Terminal outlets Before Disinfection | Before Disinfection | Pedobacter_caeni | 污水土地杆菌 |  | 0.0403 | 1 | Pedobacter | 土地杆菌属 | 64 | 73 | 0.2 | 0.24 | 77 | 87 | 105 | 87 | 119 | 100 | G- | 0.672 | 0.7744 | 1 | 0.97 | id¦19020654¦BAC¦R_5929241¦ | id¦72247450¦BAC¦S_7555586¦
D | Terminal outlets Before Disinfection | Before Disinfection | Atopobium_parvulum | 极小陌生菌 |  | 0.1414 | 1 | Atopobium | 陌生菌属 | 55 | 64 | 0.2 | 0.24 | 67 | 81 | 32 | 26 | 38 | 30 | G+ | 1.0331 | 1.2377 | 1 | 0.98 | id¦30051589¦BAC¦R_2978760¦ | id¦23054861¦BAC¦S_8819107¦
R253 | Terminal outlets After Disinfection | After Disinfection | Kytococcus_sedentarius | 久坐皮肤球菌 |  | 0.0264 | 1 | Kytococcus | 皮肤球菌属 | 11 | 14 | 0.19 | 0.23 | 20 | 24 | 17 | 9 | 20 | 12 | G+ | 0.2981 | 0.3668 | 1 | 0.97 | id¦26369276¦BAC¦R_5373022¦ | id¦69598700¦BAC¦S_1700297¦
E | Terminal outlets Before Disinfection | Before Disinfection | Caulobacter_segnis | 惰性柄杆菌 |  | 0.0975 | 1.63 | Caulobacter | 柄杆菌属 | 131 | 272 | 0.1 | 0.23 | 193 | 468 | 64 | 43 | 154 | 90 | G- | 0.6679 | 1.5984 | 0.61 | 0.3 | id¦03902742¦BAC¦R_4782067¦ | id¦42807857¦BAC¦S_2392370¦
E | Terminal outlets Before Disinfection | Before Disinfection | Caulobacter_vibrioides | 弧形柄杆菌 |  | 0.1338 | 1.02 | Caulobacter | 柄杆菌属 | 103 | 272 | 0.09 | 0.23 | 183 | 468 | 60 | 34 | 154 | 90 | G- | 0.6569 | 1.5984 | 0.98 | 0.99 | id¦55331277¦BAC¦R_4113112¦ | id¦03591998¦BAC¦S_6058582¦
R249 | Terminal outlets After Disinfection | After Disinfection | Cedecea_neteri | 耐特西地西菌 |  | 0.0314 | 1 | Cedecea | 西地西菌属 | 20 | 35 | 0.21 | 0.22 | 55 | 59 | 34 | 12 | 36 | 22 | G- | 0.364 | 0.3897 | 1 | 0.94 | id¦13870026¦BAC¦R_3246025¦ | id¦69498756¦BAC¦S_0399247¦
R249 | Terminal outlets After Disinfection | After Disinfection | Belnapia_rosea | 玫瑰别尔纳普菌 |  | 0.0399 | 1.01 | Belnapia | 别尔纳普菌属 | 29 | 36 | 0.2 | 0.22 | 67 | 77 | 41 | 18 | 47 | 22 | G- | 0.3449 | 0.3908 | 0.99 | 0.95 | id¦79305084¦BAC¦R_1478717¦ | id¦54472968¦BAC¦S_8360463¦
R253 | Terminal outlets After Disinfection | After Disinfection | Ralstonia_pickettii | 皮氏罗尔斯顿菌 |  | 0.0163 | 1 | Ralstonia | 罗尔斯顿菌属 | 17 | 31 | 0.16 | 0.22 | 31 | 41 | 26 | 14 | 34 | 26 | G- | 0.2589 | 0.3427 | 1 | 0.89 | id¦34113688¦BAC¦R_2898822¦ | id¦99940213¦BAC¦S_3917488¦
E | Terminal outlets Before Disinfection | Before Disinfection | Pseudomonas_aeruginosa | 铜绿假单胞菌 |  | 0.077 | 1.01 | Pseudomonas | 假单胞菌属 | 15 | 244 | 0.05 | 0.22 | 169 | 563 | 56 | 5 | 186 | 80 | G- | 0.3714 | 1.5207 | 0.99 | 0.98 | id¦94137680¦BAC¦R_2366448¦ | id¦01116727¦BAC¦S_0393240¦
D | Terminal outlets Before Disinfection | Before Disinfection | Solobacterium_moorei | 莫氏细小杆菌 |  | 0.1234 | 1 | Solobacterium | 细小杆菌属 | 57 | 57 | 0.2 | 0.2 | 88 | 88 | 41 | 27 | 41 | 27 | G+ | 1.0341 | 1.0341 | 1 | 0.95 | id¦42049992¦BAC¦R_9469413¦ | id¦40263554¦BAC¦S_4409501¦
D | Terminal outlets Before Disinfection | Before Disinfection | Isoptericola_variabilis | 变异白蚁菌 |  | 0.1699 | 1 | Isoptericola | 白蚁菌属 | 33 | 33 | 0.19 | 0.19 | 102 | 104 | 48 | 16 | 49 | 16 | G+ | 0.9986 | 1.0109 | 1 | 0.98 | id¦54249479¦BAC¦R_5040128¦ | id¦64495660¦BAC¦S_6274438¦
R249 | Terminal outlets After Disinfection | After Disinfection | Dolosigranulum_pigrum | 懒惰狡诈菌 |  | 0.0289 | 1 | Dolosigranulum | 狡诈菌属 | 15 | 15 | 0.19 | 0.19 | 21 | 21 | 13 | 9 | 13 | 9 | G+ | 0.3258 | 0.3258 | 1 | 0.94 | id¦43302463¦BAC¦R_3797726¦ | id¦97073597¦BAC¦S_8288378¦
D | Terminal outlets Before Disinfection | Before Disinfection | Megasphaera_micronuciformis | 小核桃形巨球形菌 |  | 0.1673 | 1 | Megasphaera | 巨球形菌属 | 64 | 65 | 0.18 | 0.19 | 72 | 73 | 34 | 30 | 34 | 31 | G- | 0.9644 | 0.9741 | 1 | 1 | id¦19311532¦BAC¦R_5484464¦ | id¦79476155¦BAC¦S_5745555¦
B | Terminal outlets Before Disinfection | Before Disinfection | Acidovorax_temperans | 温和食酸菌 |  | 0.0166 | 1 | Acidovorax | 食酸菌属 | 12 | 17 | 0.1 | 0.19 | 22 | 44 | 30 | 16 | 60 | 23 | G- | 0.3231 | 0.6392 | 1 | 0.96 | id¦02810628¦BAC¦R_8344044¦ | id¦27147656¦BAC¦S_4831994¦
D | Terminal outlets Before Disinfection | Before Disinfection | Lawsonella_clevelandensis | - |  | 0.1598 | 1 | Lawsonella | - | 62 | 62 | 0.18 | 0.18 | 64 | 64 | 30 | 29 | 30 | 29 | G+ | 0.9473 | 0.9473 | 1 | 0.99 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
B | Terminal outlets Before Disinfection | Before Disinfection | Blautia_producta | 延长布劳特菌 |  | 0.0287 | 1 | Blautia | 布劳特菌属 | 23 | 26 | 0.16 | 0.18 | 28 | 32 | 38 | 31 | 44 | 36 | G+ | 0.5141 | 0.5898 | 1 | 0.93 | id¦08578919¦BAC¦R_8452509¦ | id¦45628065¦BAC¦S_5116168¦
B | Terminal outlets Before Disinfection | Before Disinfection | Pelomonas_puraquae | - |  | 0.0303 | 1 | Pelomonas | - | 34 | 37 | 0.15 | 0.18 | 45 | 51 | 61 | 46 | 70 | 51 | G- | 0.5075 | 0.5785 | 1 | 1 | id¦47005438¦BAC¦R_6576497¦ | id¦00827443¦BAC¦S_8432294¦
E | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_saprophyticus | 腐生葡萄球菌 |  | 0.0913 | 1.02 | Staphylococcus | 葡萄球菌属 | 56 | 179 | 0.06 | 0.18 | 65 | 196 | 21 | 18 | 65 | 59 | G+ | 0.3924 | 1.2348 | 0.98 | 0.96 | id¦98444782¦BAC¦R_2947762¦ | id¦00356610¦BAC¦S_9745064¦
E | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_pettenkoferi | 佩滕科夫葡萄球菌 |  | 0.0414 | 1 | Staphylococcus | 葡萄球菌属 | 21 | 179 | 0.03 | 0.18 | 29 | 196 | 10 | 7 | 65 | 59 | G+ | 0.1882 | 1.2348 | 1 | 0.99 | id¦39979974¦BAC¦R_3584980¦ | id¦43498178¦BAC¦S_8828073¦
E | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_hominis | 人葡萄球菌 |  | 0.0339 | 1 | Staphylococcus | 葡萄球菌属 | 20 | 179 | 0.03 | 0.18 | 25 | 196 | 8 | 7 | 65 | 59 | G+ | 0.1765 | 1.2348 | 1 | 0.96 | id¦21131355¦BAC¦R_7789825¦ | id¦01588904¦BAC¦S_1607535¦
E | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_capitis | 头葡萄球菌 |  | 0.0306 | 1 | Staphylococcus | 葡萄球菌属 | 17 | 179 | 0.02 | 0.18 | 21 | 196 | 7 | 6 | 65 | 59 | G+ | 0.1402 | 1.2348 | 1 | 0.88 | id¦91254114¦BAC¦R_4675524¦ | id¦78222658¦BAC¦S_6642837¦
E | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_epidermidis | 表皮葡萄球菌 |  | 0.018 | 1 | Staphylococcus | 葡萄球菌属 | 13 | 179 | 0.01 | 0.18 | 16 | 196 | 5 | 4 | 65 | 59 | G+ | 0.0944 | 1.2348 | 1 | 0.84 | id¦15608884¦BAC¦R_9898902¦ | id¦81948656¦BAC¦S_6145183¦
E | Terminal outlets Before Disinfection | Before Disinfection | Staphylococcus_haemolyticus | 溶血葡萄球菌 |  | 0.0171 | 1 | Staphylococcus | 葡萄球菌属 | 12 | 179 | 0.01 | 0.18 | 15 | 196 | 5 | 4 | 65 | 59 | G+ | 0.0916 | 1.2348 | 1 | 0.97 | id¦33823453¦BAC¦R_4061613¦ | id¦21767703¦BAC¦S_6480655¦
B | Terminal outlets Before Disinfection | Before Disinfection | Cloacibacterium_normanense | - |  | 0.0218 | 1 | Cloacibacterium | - | 14 | 14 | 0.17 | 0.17 | 23 | 23 | 31 | 19 | 31 | 19 | G- | 0.5693 | 0.5693 | 1 | 0.92 | id¦08036817¦BAC¦R_0859119¦ | id¦36590735¦BAC¦S_8513847¦
D | Terminal outlets Before Disinfection | Before Disinfection | Treponema_denticola | 齿垢密螺旋体 |  | 0.0388 | 1 | Treponema | 密螺旋体属 | 33 | 80 | 0.09 | 0.17 | 56 | 108 | 26 | 16 | 51 | 38 | G- | 0.4639 | 0.9148 | 1 | 0.99 | id¦80442506¦BAC¦R_5573683¦ | id¦44349785¦BAC¦S_0051667¦
D | Terminal outlets Before Disinfection | Before Disinfection | Treponema_socranskii | 索氏密螺旋体 |  | 0.0115 | 1 | Treponema | 密螺旋体属 | 11 | 80 | 0.02 | 0.17 | 12 | 108 | 6 | 5 | 51 | 38 | G- | 0.1002 | 0.9148 | 1 | 0.95 | id¦16061814¦BAC¦R_1848126¦ | id¦09144440¦BAC¦S_7465830¦
E | Terminal outlets Before Disinfection | Before Disinfection | Enhydrobacter_aerosaccus | 气囊栖水菌 |  | 0.1837 | 1.57 | Enhydrobacter | 栖水菌属 | 250 | 250 | 0.16 | 0.16 | 469 | 469 | 155 | 82 | 155 | 82 | G- | 1.1418 | 1.1418 | 0.64 | 0.68 | id¦19544319¦BAC¦R_9865596¦ | id¦15638415¦BAC¦S_7626718¦
D | Terminal outlets Before Disinfection | Before Disinfection | Sanguibacter_keddieii | 科氏血杆菌 |  | 0.14 | 1 | Sanguibacter | 血杆菌属 | 20 | 20 | 0.15 | 0.15 | 81 | 81 | 38 | 9 | 38 | 9 | G+ | 0.8108 | 0.8108 | 1 | 0.95 | id¦43012025¦BAC¦R_2392898¦ | id¦53530719¦BAC¦S_9806900¦
E | Terminal outlets Before Disinfection | Before Disinfection | Pelomonas_puraquae | - |  | 0.2293 | 1.01 | Pelomonas | - | 253 | 270 | 0.13 | 0.15 | 334 | 388 | 110 | 83 | 128 | 89 | G- | 0.9086 | 1.0627 | 0.99 | 1 | id¦47005438¦BAC¦R_6576497¦ | id¦00827443¦BAC¦S_8432294¦
E | Terminal outlets Before Disinfection | Before Disinfection | Acinetobacter_baumannii | 鲍曼不动杆菌 |  | 0.0481 | 1 | Acinetobacter | 不动杆菌属 | 40 | 215 | 0.04 | 0.15 | 69 | 241 | 23 | 13 | 79 | 71 | G- | 0.272 | 1.0718 | 1 | 0.98 | id¦96500901¦BAC¦R_6463796¦ | id¦50407874¦BAC¦S_9440389¦
E | Terminal outlets Before Disinfection | Before Disinfection | Acinetobacter_junii | 琼氏不动杆菌 |  | 0.0352 | 1.03 | Acinetobacter | 不动杆菌属 | 28 | 215 | 0.03 | 0.15 | 43 | 241 | 14 | 9 | 79 | 71 | G- | 0.2127 | 1.0718 | 0.97 | 0.99 | id¦82944583¦BAC¦R_4556625¦ | id¦62389735¦BAC¦S_6702589¦
E | Terminal outlets Before Disinfection | Before Disinfection | Acinetobacter_tandoii | 坦氏不动杆菌 |  | 0.0119 | 1 | Acinetobacter | 不动杆菌属 | 14 | 215 | 0.01 | 0.15 | 17 | 241 | 6 | 5 | 79 | 71 | G- | 0.079 | 1.0718 | 1 | 0.99 | id¦82120165¦BAC¦R_1240279¦ | id¦96594351¦BAC¦S_3670773¦
E | Terminal outlets Before Disinfection | Before Disinfection | Phreatobacter_oligotrophus | - |  | 0.1244 | 1.07 | Phreatobacter | - | 59 | 70 | 0.08 | 0.14 | 159 | 308 | 52 | 19 | 101 | 23 | G- | 0.5367 | 0.976 | 0.93 | 1 | id¦55167328¦BAC¦R_7985938¦ | id¦67117665¦BAC¦S_6681471¦
B | Terminal outlets Before Disinfection | Before Disinfection | Sphingobium_yanoikuyae | 矢野口鞘脂菌 |  | 0.0093 | 1 | Sphingobium | 鞘脂菌属 | 15 | 21 | 0.07 | 0.14 | 18 | 34 | 25 | 20 | 46 | 29 | G- | 0.2337 | 0.4714 | 1 | 0.92 | id¦41849270¦BAC¦R_6724778¦ | id¦75042391¦BAC¦S_3739105¦
E | Terminal outlets Before Disinfection | Before Disinfection | Chryseobacterium_molle | 敏感金黄杆菌 |  | 0.0578 | 1.04 | Chryseobacterium | 金黄杆菌属 | 15 | 95 | 0.03 | 0.14 | 53 | 226 | 17 | 5 | 74 | 31 | G- | 0.2363 | 0.9783 | 0.96 | 0 | id¦47796851¦BAC¦R_3744626¦ | id¦59518123¦BAC¦S_7941957¦
R249 | Terminal outlets After Disinfection | After Disinfection | Citricoccus_muralis | 壁柠檬球菌 |  | 0.0291 | 1 | Citricoccus | 柠檬球菌属 | 13 | 13 | 0.13 | 0.13 | 25 | 25 | 15 | 8 | 15 | 8 | G+ | 0.219 | 0.219 | 1 | 0.79 | id¦27014927¦BAC¦R_3170991¦ | id¦73201149¦BAC¦S_3211978¦
R253 | Terminal outlets After Disinfection | After Disinfection | Cellvibrio_mixtus | 混合纤维弧菌 |  | 0.0187 | 1 | Cellvibrio | 纤维弧菌属 | 16 | 16 | 0.13 | 0.13 | 23 | 23 | 19 | 13 | 19 | 13 | G- | 0.2 | 0.2 | 1 | 1 | id¦57437709¦BAC¦R_9566021¦ | id¦95815400¦BAC¦S_7803496¦
D | Terminal outlets Before Disinfection | Before Disinfection | Eikenella_corrodens | 侵蚀艾肯菌 |  | 0.0521 | 1 | Eikenella | 艾肯菌属 | 18 | 26 | 0.12 | 0.13 | 63 | 70 | 30 | 8 | 33 | 12 | G- | 0.6113 | 0.6974 | 1 | 0.98 | id¦61359227¦BAC¦R_1869456¦ | id¦25762185¦BAC¦S_1242390¦
D | Terminal outlets Before Disinfection | Before Disinfection | Achromobacter_xylosoxidans | 木糖氧化无色杆菌 |  | 0.0646 | 1.01 | Achromobacter | 无色杆菌属 | 62 | 153 | 0.09 | 0.13 | 139 | 199 | 65 | 29 | 94 | 72 | G- | 0.4805 | 0.6883 | 0.99 | 0.98 | id¦46056059¦BAC¦R_8923498¦ | id¦89463873¦BAC¦S_1656929¦
D | Terminal outlets Before Disinfection | Before Disinfection | Abiotrophia_defectiva | 缺陷乏养菌 |  | 0.1052 | 1 | Abiotrophia | 营养缺陷菌属 | 37 | 37 | 0.12 | 0.12 | 53 | 53 | 25 | 17 | 25 | 17 | G+ | 0.6098 | 0.6098 | 1 | 0.97 | id¦02848317¦BAC¦R_9947759¦ | id¦99770673¦BAC¦S_6049361¦
B | Terminal outlets Before Disinfection | Before Disinfection | Ralstonia_pickettii | 皮氏罗尔斯顿菌 |  | 0.0117 | 1 | Ralstonia | 罗尔斯顿菌属 | 17 | 24 | 0.1 | 0.12 | 26 | 31 | 36 | 23 | 42 | 33 | G- | 0.3387 | 0.3991 | 1 | 0.99 | id¦53230913¦BAC¦R_4512424¦ | id¦99940213¦BAC¦S_3917488¦
R249 | Terminal outlets After Disinfection | After Disinfection | Kineococcus_xinjiangensis | 新疆动球菌 |  | 0.0229 | 1 | Kineococcus | 动球菌属 | 16 | 17 | 0.1 | 0.12 | 26 | 31 | 16 | 10 | 19 | 10 | G+ | 0.1736 | 0.204 | 1 | 0.97 | id¦14524591¦BAC¦R_6153165¦ | id¦97422565¦BAC¦S_9169032¦
R249 | Terminal outlets After Disinfection | After Disinfection | Paenibacillus_barengoltzii | 巴伦氏类芽胞杆菌 |  | 0.0156 | 1 | Paenibacillus | 类芽胞杆菌属 | 21 | 25 | 0.09 | 0.12 | 24 | 35 | 15 | 13 | 22 | 15 | G+ | 0.1502 | 0.2042 | 1 | 0.95 | id¦65281503¦BAC¦R_6163114¦ | id¦43538642¦BAC¦S_7591604¦
E | Terminal outlets Before Disinfection | Before Disinfection | Ancylobacter_aquaticus | 水生屈曲杆菌 |  | 0.0776 | 1.42 | Ancylobacter | 屈曲杆菌属 | 20 | 26 | 0.08 | 0.12 | 172 | 257 | 57 | 7 | 85 | 9 | G- | 0.5371 | 0.8438 | 0.7 | 0.86 | id¦68470066¦BAC¦R_9029029¦ | id¦88055554¦BAC¦S_5336022¦
D | Terminal outlets Before Disinfection | Before Disinfection | Oribacterium_parvum | 小口腔杆菌 |  | 0.0523 | 1 | Oribacterium | 口腔杆菌属 | 23 | 51 | 0.06 | 0.12 | 32 | 69 | 15 | 11 | 32 | 24 | G+ | 0.3036 | 0.6435 | 1 | 0.99 | id¦41241148¦BAC¦R_1668514¦ | id¦17706216¦BAC¦S_0280564¦
D | Terminal outlets Before Disinfection | Before Disinfection | Oribacterium_sinus | 瘘管口腔杆菌 |  | 0.0294 | 1 | Oribacterium | 口腔杆菌属 | 12 | 51 | 0.03 | 0.12 | 19 | 69 | 9 | 6 | 32 | 24 | G+ | 0.1713 | 0.6435 | 1 | 0.98 | id¦44074519¦BAC¦R_6209243¦ | id¦23360470¦BAC¦S_1633770¦
D | Terminal outlets Before Disinfection | Before Disinfection | Filifactor_alocis | 龈沟产线菌 |  | 0.1017 | 1 | Filifactor | 产线菌属 | 37 | 37 | 0.11 | 0.11 | 48 | 48 | 23 | 17 | 23 | 17 | G+ | 0.5854 | 0.5854 | 1 | 1 | id¦93578193¦BAC¦R_6108560¦ | id¦82707687¦BAC¦S_8283035¦
D | Terminal outlets Before Disinfection | Before Disinfection | Lachnoanaerobaculum_saburreum | - |  | 0.0374 | 1 | Lachnoanaerobaculum | - | 13 | 51 | 0.06 | 0.11 | 37 | 68 | 17 | 6 | 32 | 24 | G+ | 0.3003 | 0.5608 | 1 | 0.95 | id¦78712898¦BAC¦R_9022791¦ | id¦00903593¦BAC¦S_5213486¦
R249 | Terminal outlets After Disinfection | After Disinfection | Rummeliibacillus_suwonensis | 水原鲁梅尔芽胞杆菌 |  | 0.0229 | 1 | Rummeliibacillus | 鲁梅尔芽胞杆菌属 | 19 | 21 | 0.1 | 0.1 | 23 | 23 | 14 | 12 | 14 | 13 | G+ | 0.1728 | 0.1728 | 1 | 0.93 | id¦66163392¦BAC¦R_7827014¦ | id¦74549441¦BAC¦S_3990851¦
D | Terminal outlets Before Disinfection | Before Disinfection | Elizabethkingia_meningoseptica | 脑膜脓毒伊丽莎白菌 |  | 0.0517 | 1 | Elizabethkingia | 伊丽莎白菌属 | 55 | 80 | 0.07 | 0.1 | 61 | 87 | 29 | 26 | 41 | 38 | G- | 0.3587 | 0.5006 | 1 | 0.97 | id¦29437060¦BAC¦R_2512742¦ | id¦71489140¦BAC¦S_7028191¦
D | Terminal outlets Before Disinfection | Before Disinfection | Dialister_pneumosintes | 侵肺戴阿李斯特菌 |  | 0.0451 | 1 | Dialister | 戴阿李斯特菌属 | 11 | 26 | 0.05 | 0.1 | 14 | 32 | 7 | 5 | 15 | 12 | G- | 0.2588 | 0.4989 | 1 | 0.97 | id¦70618782¦BAC¦R_4139432¦ | id¦88301161¦BAC¦S_1220072¦
D | Terminal outlets Before Disinfection | Before Disinfection | Dialister_invisus | 浑浊戴阿李斯特菌 |  | 0.0238 | 1 | Dialister | 戴阿李斯特菌属 | 11 | 26 | 0.03 | 0.1 | 14 | 32 | 7 | 5 | 15 | 12 | G- | 0.174 | 0.4989 | 1 | 0.99 | id¦52430504¦BAC¦R_4469690¦ | id¦84924046¦BAC¦S_6592800¦
R249 | Terminal outlets After Disinfection | After Disinfection | Alkanindiges_illinoisensis | - |  | 0.0148 | 1 | Alkanindiges | - | 11 | 11 | 0.09 | 0.09 | 15 | 15 | 9 | 7 | 9 | 7 | G- | 0.1516 | 0.1516 | 1 | 0.94 | id¦23591877¦BAC¦R_4574919¦ | id¦30269641¦BAC¦S_3485358¦
D | Terminal outlets Before Disinfection | Before Disinfection | Kytococcus_sedentarius | 久坐皮肤球菌 |  | 0.0546 | 1 | Kytococcus | 皮肤球菌属 | 11 | 13 | 0.08 | 0.09 | 43 | 46 | 20 | 5 | 22 | 6 | G+ | 0.4289 | 0.4581 | 1 | 0.97 | id¦93281679¦BAC¦R_8808154¦ | id¦69598700¦BAC¦S_1700297¦
E | Terminal outlets Before Disinfection | Before Disinfection | Comamonas_aquatica | 水生丛毛单胞菌 |  | 0.0676 | 1 | Comamonas | 丛毛单胞菌属 | 69 | 102 | 0.06 | 0.09 | 101 | 168 | 33 | 23 | 55 | 34 | G- | 0.4221 | 0.6473 | 1 | 0.98 | id¦26802777¦BAC¦R_1114359¦ | id¦51095929¦BAC¦S_7965541¦
D | Terminal outlets Before Disinfection | Before Disinfection | Methylorubrum_rhodinum | - |  | 0.0377 | 1 | Methylorubrum | - | 16 | 32 | 0.04 | 0.09 | 28 | 86 | 13 | 8 | 41 | 15 | G- | 0.2183 | 0.4618 | 1 | 0.72 | id¦82173618¦BAC¦R_5525052¦ | id¦99705343¦BAC¦S_6341165¦
D | Terminal outlets Before Disinfection | Before Disinfection | Weissella_confusa | 混淆魏斯菌 |  | 0.061 | 1 | Weissella | 魏斯菌属 | 38 | 41 | 0.08 | 0.08 | 40 | 42 | 19 | 18 | 20 | 19 | G+ | 0.4019 | 0.4207 | 1 | 0.96 | id¦49501346¦BAC¦R_8080235¦ | id¦05050526¦BAC¦S_4884511¦
D | Terminal outlets Before Disinfection | Before Disinfection | Aerococcus_urinae | 尿气球菌 |  | 0.0646 | 1.08 | Aerococcus | 气球菌属 | 25 | 25 | 0.08 | 0.08 | 45 | 45 | 21 | 12 | 21 | 12 | G+ | 0.4036 | 0.4036 | 0.93 | 0.95 | id¦24449035¦BAC¦R_0941850¦ | id¦46892321¦BAC¦S_9758766¦
E | Terminal outlets Before Disinfection | Before Disinfection | Pseudolabrys_taiwanensis | 台湾假双头斧形菌 |  | 0.126 | 1.15 | Pseudolabrys | 假双头斧形菌属 | 13 | 13 | 0.08 | 0.08 | 196 | 196 | 65 | 4 | 65 | 4 | G- | 0.5773 | 0.5773 | 0.87 | 1 | id¦34647878¦BAC¦R_5460791¦ | id¦07849103¦BAC¦S_1168093¦
D | Terminal outlets Before Disinfection | Before Disinfection | Kingella_denitrificans | 脱氮金氏菌 |  | 0.0321 | 1 | Kingella | 金氏菌属 | 14 | 20 | 0.06 | 0.08 | 27 | 36 | 13 | 7 | 17 | 9 | G- | 0.3157 | 0.4083 | 1 | 0.86 | id¦71403626¦BAC¦R_8045734¦ | id¦53555355¦BAC¦S_5403951¦
E | Terminal outlets Before Disinfection | Before Disinfection | Chelatococcus_asaccharovorans | 不噬糖螯合球菌 |  | 0.0688 | 1.05 | Chelatococcus | 螯合球菌属 | 84 | 85 | 0.04 | 0.08 | 126 | 189 | 42 | 28 | 62 | 28 | G- | 0.2862 | 0.5278 | 0.95 | 0.56 | id¦37001757¦BAC¦R_4669271¦ | id¦29006020¦BAC¦S_0604929¦
D | Terminal outlets Before Disinfection | Before Disinfection | Tannerella_forsythia | 福赛斯坦纳菌 |  | 0.061 | 1 | Tannerella | 坦纳菌属 | 43 | 43 | 0.07 | 0.07 | 54 | 54 | 25 | 20 | 25 | 20 | G- | 0.3734 | 0.3734 | 1 | 0.97 | id¦69700064¦BAC¦R_0104713¦ | id¦17537020¦BAC¦S_3544120¦
E | Terminal outlets Before Disinfection | Before Disinfection | Pedobacter_caeni | 污水土地杆菌 |  | 0.082 | 1.01 | Pedobacter | 土地杆菌属 | 124 | 144 | 0.05 | 0.07 | 155 | 219 | 51 | 41 | 72 | 47 | G- | 0.3263 | 0.5193 | 0.99 | 1 | id¦19020654¦BAC¦R_5929241¦ | id¦72247450¦BAC¦S_7555586¦
D | Terminal outlets Before Disinfection | Before Disinfection | Chryseobacterium_arthrosphaerae | 千足虫金黄杆菌 |  | 0.0199 | 1 | Chryseobacterium | 金黄杆菌属 | 29 | 56 | 0.03 | 0.07 | 35 | 73 | 16 | 14 | 34 | 26 | G- | 0.1537 | 0.36 | 1 | 0.95 | id¦90719933¦BAC¦R_2189061¦ | id¦89195945¦BAC¦S_4037851¦
D | Terminal outlets Before Disinfection | Before Disinfection | Stomatobaculum_longum | - |  | 0.0525 | 1 | Stomatobaculum | - | 20 | 20 | 0.06 | 0.06 | 30 | 30 | 14 | 9 | 14 | 9 | Gram-variable | 0.306 | 0.306 | 1 | 0.97 | id¦87561998¦BAC¦R_7066577¦ | id¦80920162¦BAC¦S_5042249¦
R249 | Terminal outlets After Disinfection | After Disinfection | Pluralibacter_gergoviae | 日勾维多源杆菌 |  | 0.0097 | 1.07 | Pluralibacter | 多源杆菌属 | 11 | 11 | 0.06 | 0.06 | 18 | 19 | 11 | 7 | 12 | 7 | G- | 0.1011 | 0.1075 | 0.93 | 0.9 | id¦90213458¦BAC¦R_7018829¦ | id¦01873914¦BAC¦S_7273219¦
E | Terminal outlets Before Disinfection | Before Disinfection | Moraxella_osloensis | 奥斯陆莫拉菌 |  | 0.0451 | 1 | Moraxella | 莫拉菌属 | 56 | 61 | 0.05 | 0.06 | 69 | 73 | 23 | 18 | 24 | 20 | G- | 0.3811 | 0.4096 | 1 | 1 | id¦78445804¦BAC¦R_1006151¦ | id¦03018125¦BAC¦S_5034603¦
E | Terminal outlets Before Disinfection | Before Disinfection | Kocuria_palustris | 沼泽库克菌 |  | 0.0365 | 1 | Kocuria | 库克菌属 | 21 | 58 | 0.02 | 0.06 | 30 | 82 | 10 | 7 | 27 | 19 | G+ | 0.1744 | 0.4107 | 1 | 0.96 | id¦86496397¦BAC¦R_2264120¦ | id¦65461644¦BAC¦S_9118994¦
D | Terminal outlets Before Disinfection | Before Disinfection | Enhydrobacter_aerosaccus | 气囊栖水菌 |  | 0.0426 | 1.06 | Enhydrobacter | 栖水菌属 | 47 | 47 | 0.05 | 0.05 | 75 | 75 | 35 | 22 | 35 | 22 | G- | 0.261 | 0.261 | 0.94 | 0.44 | id¦19544319¦BAC¦R_9865596¦ | id¦15638415¦BAC¦S_7626718¦
E | Terminal outlets Before Disinfection | Before Disinfection | Lawsonella_clevelandensis | - |  | 0.0924 | 1 | Lawsonella | - | 35 | 35 | 0.05 | 0.05 | 35 | 35 | 12 | 12 | 12 | 12 | G+ | 0.3625 | 0.3625 | 1 | 0.99 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
E | Terminal outlets Before Disinfection | Before Disinfection | Pseudorhodoplanes_sinuspersici | 波斯湾假红游动菌 |  | 0.0729 | 1.27 | Pseudorhodoplanes | 假红游动菌属 | 14 | 14 | 0.05 | 0.05 | 135 | 135 | 44 | 5 | 44 | 5 | G- | 0.3725 | 0.3725 | 0.79 | 0.99 | id¦61237527¦BAC¦R_8143218¦ | id¦03886686¦BAC¦S_7235351¦
R249 | Terminal outlets After Disinfection | After Disinfection | Metabacillus_halosaccharovorans | - |  | 0.0114 | 1 | Metabacillus | - | 12 | 13 | 0.05 | 0.05 | 15 | 16 | 9 | 7 | 10 | 8 | G+ | 0.0857 | 0.0916 | 1 | 0.88 | id¦13549792¦BAC¦R_0336287¦ | id¦87160758¦BAC¦S_6883356¦
E | Terminal outlets Before Disinfection | Before Disinfection | Ralstonia_pickettii | 皮氏罗尔斯顿菌 |  | 0.0311 | 1.07 | Ralstonia | 罗尔斯顿菌属 | 56 | 71 | 0.04 | 0.05 | 94 | 115 | 31 | 18 | 38 | 23 | G- | 0.3116 | 0.3836 | 0.94 | 0.96 | id¦34113688¦BAC¦R_2898822¦ | id¦99940213¦BAC¦S_3917488¦
D | Terminal outlets Before Disinfection | Before Disinfection | Parabacteroides_distasonis | 迪氏副拟杆菌 |  | 0.0219 | 1.02 | Parabacteroides | 副拟杆菌属 | 30 | 37 | 0.03 | 0.05 | 39 | 57 | 18 | 14 | 27 | 17 | G- | 0.1681 | 0.2476 | 0.98 | 0.95 | id¦75610586¦BAC¦R_5931063¦ | id¦66867688¦BAC¦S_5131031¦
E | Terminal outlets Before Disinfection | Before Disinfection | Rothia_mucilaginosa | 黏液罗氏菌 |  | 0.0275 | 1 | Rothia | 罗氏菌属 | 31 | 44 | 0.03 | 0.05 | 33 | 48 | 11 | 10 | 16 | 14 | G+ | 0.2371 | 0.3374 | 1 | 0.99 | id¦25827608¦BAC¦R_0635913¦ | id¦64873621¦BAC¦S_0860975¦
E | Terminal outlets Before Disinfection | Before Disinfection | Reyranella_soli | - |  | 0.0474 | 1.11 | Reyranella | - | 15 | 18 | 0.03 | 0.05 | 127 | 168 | 42 | 5 | 55 | 6 | G- | 0.213 | 0.33 | 0.9 | 0.99 | id¦50328797¦BAC¦R_4386186¦ | id¦63520749¦BAC¦S_9002388¦
E | Terminal outlets Before Disinfection | Before Disinfection | Rhodopila_globiformis | - |  | 0.0374 | 1.67 | Rhodopila | - | 17 | 17 | 0.04 | 0.04 | 110 | 110 | 36 | 6 | 36 | 6 | G- | 0.25 | 0.25 | 0.6 | 0.67 | id¦97057660¦BAC¦R_8892021¦ | id¦22726187¦BAC¦S_8027602¦
E | Terminal outlets Before Disinfection | Before Disinfection | Vibrionimonas_magnilacihabitans | - |  | 0.0622 | 1.06 | Vibrionimonas | - | 13 | 13 | 0.04 | 0.04 | 65 | 65 | 21 | 4 | 21 | 4 | G- | 0.265 | 0.265 | 0.94 | 0.73 | id¦40141315¦BAC¦R_0342398¦ | id¦54164186¦BAC¦S_5701059¦
D | Terminal outlets Before Disinfection | Before Disinfection | Pelomonas_puraquae | - |  | 0.0257 | 1 | Pelomonas | - | 29 | 33 | 0.03 | 0.04 | 38 | 50 | 18 | 14 | 24 | 16 | G- | 0.1478 | 0.1968 | 1 | 0.98 | id¦47005438¦BAC¦R_6576497¦ | id¦00827443¦BAC¦S_8432294¦
D | Terminal outlets Before Disinfection | Before Disinfection | Caulobacter_segnis | 惰性柄杆菌 |  | 0.0155 | 1 | Caulobacter | 柄杆菌属 | 13 | 20 | 0.02 | 0.04 | 18 | 43 | 8 | 6 | 20 | 9 | G- | 0.089 | 0.2161 | 1 | 0 | id¦03902742¦BAC¦R_4782067¦ | id¦42807857¦BAC¦S_2392370¦
D | Terminal outlets Before Disinfection | Before Disinfection | Methylovulum_psychrotolerans | - |  | 0.0165 | 1.72 | Methylovulum | - | 25 | 25 | 0.03 | 0.03 | 34 | 34 | 16 | 12 | 16 | 12 | G- | 0.1626 | 0.1626 | 0.58 | 0 | id¦96177612¦BAC¦R_9656588¦ | id¦21563331¦BAC¦S_0320011¦
D | Terminal outlets Before Disinfection | Before Disinfection | Faecalibacterium_prausnitzii | 普拉栖粪杆菌 |  | 0.0145 | 1 | Faecalibacterium | 栖粪杆菌属 | 12 | 12 | 0.03 | 0.03 | 21 | 21 | 10 | 6 | 10 | 6 | - | 0.1745 | 0.1745 | 1 | 0.86 | id¦97955161¦BAC¦R_5286549¦ | id¦48436959¦BAC¦S_2604329¦
D | Terminal outlets Before Disinfection | Before Disinfection | Gemmiger_formicilis | 甲酸芽殖菌 |  | 0.0224 | 1 | Gemmiger | 芽殖菌属 | 12 | 12 | 0.03 | 0.03 | 22 | 22 | 10 | 6 | 10 | 6 | G- | 0.1598 | 0.1598 | 1 | 0.97 | id¦92887880¦BAC¦R_5789399¦ | id¦91539137¦BAC¦S_6185118¦
E | Terminal outlets Before Disinfection | Before Disinfection | Haemophilus_parainfluenzae | 副流感嗜血杆菌 |  | 0.0197 | 1 | Haemophilus | 嗜血杆菌属 | 17 | 22 | 0.03 | 0.03 | 23 | 29 | 8 | 6 | 10 | 7 | G- | 0.1782 | 0.2272 | 1 | 0.82 | id¦16059935¦BAC¦R_6721919¦ | id¦77177367¦BAC¦S_3784721¦
D | Terminal outlets Before Disinfection | Before Disinfection | Pedobacter_caeni | 污水土地杆菌 |  | 0.0225 | 1 | Pedobacter | 土地杆菌属 | 37 | 42 | 0.02 | 0.03 | 43 | 46 | 20 | 17 | 22 | 20 | G- | 0.1294 | 0.1408 | 1 | 0.99 | id¦19020654¦BAC¦R_5929241¦ | id¦72247450¦BAC¦S_7555586¦
E | Terminal outlets Before Disinfection | Before Disinfection | Blastococcus_saxobsidens | 居岩芽生球菌 |  | 0.0255 | 1 | Blastococcus | 芽生球菌属 | 12 | 19 | 0.02 | 0.03 | 40 | 64 | 13 | 4 | 21 | 6 | G+ | 0.1615 | 0.2445 | 1 | 0.97 | id¦75982189¦BAC¦R_3496942¦ | id¦28838149¦BAC¦S_5089509¦
D | Terminal outlets Before Disinfection | Before Disinfection | Bilophila_wadsworthia | 沃兹沃嗜胆菌 |  | 0.0159 | 1 | Bilophila | 嗜胆菌属 | 19 | 19 | 0.02 | 0.02 | 19 | 19 | 9 | 9 | 9 | 9 | G- | 0.1019 | 0.1019 | 1 | 1 | id¦06383151¦BAC¦R_2822663¦ | id¦74772053¦BAC¦S_7679535¦
D | Terminal outlets Before Disinfection | Before Disinfection | Legionella_pneumophila | 嗜肺军团菌 |  | 0.0193 | 1 | Legionella | 军团菌属 | 13 | 16 | 0.02 | 0.02 | 18 | 20 | 8 | 6 | 9 | 8 | G- | 0.1195 | 0.1303 | 1 | 0.98 | id¦93409169¦BAC¦R_6167418¦ | id¦11452093¦BAC¦S_1155035¦
D | Terminal outlets Before Disinfection | Before Disinfection | Pseudopropionibacterium_propionicum | 丙酸假丙酸杆菌 |  | 0.0201 | 1 | Pseudopropionibacterium | 假丙酸杆菌属 | 15 | 15 | 0.02 | 0.02 | 18 | 18 | 8 | 7 | 8 | 7 | G+ | 0.1229 | 0.1229 | 1 | 0.96 | id¦99054358¦BAC¦R_3901657¦ | id¦52585911¦BAC¦S_0239393¦
D | Terminal outlets Before Disinfection | Before Disinfection | Catonella_morbi | 疾病卡托菌 |  | 0.0185 | 1 | Catonella | 卡托菌属 | 12 | 12 | 0.02 | 0.02 | 16 | 16 | 8 | 6 | 8 | 6 | G+ | 0.1084 | 0.1084 | 1 | 1 | id¦33511213¦BAC¦R_1927648¦ | id¦83613604¦BAC¦S_4197249¦
E | Terminal outlets Before Disinfection | Before Disinfection | Cedecea_neteri | 耐特西地西菌 |  | 0.0126 | 1 | Cedecea | 西地西菌属 | 15 | 20 | 0.01 | 0.02 | 26 | 30 | 9 | 5 | 10 | 7 | G- | 0.0919 | 0.1056 | 1 | 0.97 | id¦13870026¦BAC¦R_3246025¦ | id¦69498756¦BAC¦S_0399247¦
E | Terminal outlets Before Disinfection | Before Disinfection | Brevibacterium_casei | 乳酪短杆菌 |  | 0.0142 | 1 | Brevibacterium | 短杆菌属 | 16 | 16 | 0.01 | 0.02 | 17 | 24 | 6 | 5 | 8 | 5 | G+ | 0.0729 | 0.1058 | 1 | 0.82 | id¦49274990¦BAC¦R_4601401¦ | id¦50364648¦BAC¦S_0402074¦
E | Terminal outlets Before Disinfection | Before Disinfection | Serinicoccus_profundi | 深海丝氨酸球菌 |  | 0.0224 | 1.02 | Serinicoccus | 丝氨酸球菌属 | 11 | 12 | 0.01 | 0.02 | 19 | 23 | 6 | 4 | 8 | 4 | G+ | 0.0901 | 0.1092 | 0.98 | 0.9 | id¦43464208¦BAC¦R_0602118¦ | id¦07067620¦BAC¦S_2017242¦
D | Terminal outlets Before Disinfection | Before Disinfection | Ruthenibacterium_lactatiformans | - |  | 0.013 | 1 | Ruthenibacterium | - | 13 | 13 | 0.01 | 0.01 | 14 | 14 | 7 | 6 | 7 | 6 | G+ | 0.0746 | 0.0746 | 1 | 0.97 | id¦96204136¦BAC¦R_7225832¦ | id¦02583644¦BAC¦S_6908357¦
D | Terminal outlets Before Disinfection | Before Disinfection | [Eubacterium]_sulci | 龈沟真杆菌 |  | 0.2054 | 1.01 | - | - | 68 |  | 0.23 |  | 88 |  | 41 | 32 |  |  | G+ | 1.1915 |  | 0.99 | 1 | id¦39341315¦BAC¦R_5538451¦ | id¦83345205¦BAC¦S_5240668¦
D | Terminal outlets Before Disinfection | Before Disinfection | [Eubacterium]_brachy | 短真杆菌 |  | 0.1523 | 1.01 | - | - | 52 |  | 0.17 |  | 58 |  | 27 | 24 |  |  | G+ | 0.8857 |  | 0.99 | 0.99 | id¦95834188¦BAC¦R_9741613¦ | id¦04666549¦BAC¦S_8154038¦
D | Terminal outlets Before Disinfection | Before Disinfection | [Eubacterium]_nodatum | 缠结真杆菌 |  | 0.0807 | 1 | - | - | 25 |  | 0.09 |  | 36 |  | 17 | 12 |  |  | G+ | 0.4642 |  | 1 | 1 | id¦40386419¦BAC¦R_6865287¦ | id¦46123053¦BAC¦S_6958944¦
D | Terminal outlets Before Disinfection | Before Disinfection | [Eubacterium]_infirmum | 娇弱真杆菌 |  | 0.0446 | 1 | - | - | 11 |  | 0.05 |  | 21 |  | 10 | 5 |  |  | G+ | 0.2593 |  | 1 | 0.92 | id¦22524426¦BAC¦R_9316256¦ | id¦73178019¦BAC¦S_5528485¦

## mNGS-virus
#Sample | Latin | Chinese | Level | Coverage | CovRate | Depth | Latin_mrn | Latin_smrn | SubTypeLatin | SubTypeChi | TypeLatin | TypeChi | SpeLatin | SpeChi | STP_MRN | STP_SMRN | TP_MRN | TP_SMRN | S_MRN | S_SMRN | SDLatin_mrn | SDLatin_smrn | SDSTP_MRN | SDSTP_SMRN | SDTP_MRN | SDTP_SMRN | SDS_MRN | SDS_SMRN | VType | Latin_Re_Abu | Latin_Abs_Abu | STP_Re_Abu | TP_Re_Abu | S_Re_Abu | STP_Abs_Abu | TP_Abs_Abu | S_Abs_Abu | Depth_Ratio | Shannon_index | RefID | LatinID
D | Human_alphaherpesvirus_1 | 人类α疱疹病毒1型(HSV1) | species | 25831/149261 | 17.31 | 1.14 | 919 | 790 | - | - | - | - | Human_alphaherpesvirus_1 | 人类α疱疹病毒1型(HSV1) | - | - | - | - | 919 | 790 | 433 | 372 | - | - | - | - | 433 | 372 | dsDNA | 28.09 | 0.145 | - | - | 28.09 | - | - | 0.145 | 0.97 | 1 | id¦01736022¦VIR¦R_6645881¦ | id¦67271328¦VIR¦S_2298086¦

## mNGS-parasite
#Sample | Latin | Chinese | Coverage | CovRate | Depth | Latin_mrn | Latin_smrn | GenusLatin | GenusChi | G_MRN | G_SMRN | SDLatin_mrn | SDLatin_smrn | SDG_MRN | SDG_SMRN | Latin_Re_Abu | Genus_Re_Abu | Latin_Abs_Abu | Genus_Abs_Abu | Depth_Ratio | Shannon_index | RefID | LatinID
B | Acanthamoeba_palestinensis | 棘阿米巴* | 16383/95005146 | 0.0172 | 1.11 | 443 | 367 | Acanthamoeba | 棘阿米巴属 | 446 | 368 | 605 | 501 | 609 | 503 | 97.61 | 98.31 | 0.3185 | 0.3208 | 0.9 | 0.66 | id¦54623093¦PARA¦R_2257846¦ | id¦54693253¦PARA¦S_7369984¦

## mNGS-source water
#Sample | Latin | Chinese | Coverage | CovRate | Depth | Latin_mrn | Latin_smrn | GenusLatin | GenusChi | G_MRN | G_SMRN | SDLatin_mrn | SDLatin_smrn | SDG_MRN | SDG_SMRN | Gram | Latin_Re_Abu | Genus_Re_Abu | Latin_Abs_Abu | Genus_Abs_Abu | Depth_Ratio | Shannon_index | RefID | LatinID
source water1 | Cutibacterium_acnes | 痤疮丙酸杆菌 | 1309/2767954 | 0.0473 | 1 | 38 | 31 | Cutibacterium | - | 44 | 41 | 41 | 34 | 48 | 44 | G+ | 16.37 | 19.22 | 0.7427 | 0.8721 | 1 | 0.98 | id¦02232421¦BAC¦R_0093761¦ | id¦13032130¦BAC¦S_3713127¦
source water1 | Cutibacterium_avidum | - | 41/2627192 | 0.0016 | 1 | 2 | 2 | Cutibacterium | - | 44 | 41 | 2 | 2 | 48 | 44 | G+ | 0.91 | 19.22 | 0.0412 | 0.8721 | - | - | id¦05801907¦BAC¦R_7583150¦ | id¦18251146¦BAC¦S_8963193¦
source water1 | [Propionibacterium]_humerusii | 丙酸杆菌* | 82/2641596 | 0.0031 | 1 | 2 | 2 | Cutibacterium | - | 44 | 41 | 2 | 2 | 48 | 44 | G+ | 0.9 | 19.22 | 0.041 | 0.8721 | - | - | id¦86513342¦BAC¦R_5508967¦ | id¦75777035¦BAC¦S_4250800¦
source water1 | [Propionibacterium]_namnetense | - | 41/2431162 | 0.0017 | 1 | 1 | 1 | Cutibacterium | - | 44 | 41 | 1 | 1 | 48 | 44 | G+ | 0.49 | 19.22 | 0.0223 | 0.8721 | - | - | id¦98833027¦BAC¦R_8182154¦ | id¦85186092¦BAC¦S_0590636¦
source water1 | Acinetobacter_guillouiae | 吉洛不动杆菌 | 123/4651698 | 0.0026 | 1 | 4 | 3 | Acinetobacter | 不动杆菌属 | 17 | 14 | 4 | 3 | 18 | 15 | G- | 1.03 | 5.3 | 0.0465 | 0.2402 | - | - | id¦17019701¦BAC¦R_4174826¦ | id¦21540812¦BAC¦S_4100554¦
source water1 | Acinetobacter_junii | 琼氏不动杆菌 | 164/3447055 | 0.0048 | 1 | 5 | 2 | Acinetobacter | 不动杆菌属 | 17 | 14 | 5 | 2 | 18 | 15 | G- | 1.73 | 5.3 | 0.0785 | 0.2402 | 1 | 0.95 | id¦02713093¦BAC¦R_0113532¦ | id¦62389735¦BAC¦S_6702589¦
source water1 | Acinetobacter_ursingii | 乌尔辛不动杆菌 | 82/3545950 | 0.0023 | 1 | 2 | 2 | Acinetobacter | 不动杆菌属 | 17 | 14 | 2 | 2 | 18 | 15 | G- | 0.67 | 5.3 | 0.0305 | 0.2402 | - | - | id¦30544241¦BAC¦R_3966508¦ | id¦58318179¦BAC¦S_7032917¦
source water1 | Acinetobacter_bereziniae | 贝雷占不动杆菌 | 41/4741922 | 0.0009 | 1 | 1 | 1 | Acinetobacter | 不动杆菌属 | 17 | 14 | 1 | 1 | 18 | 15 | G- | 0.25 | 5.3 | 0.0114 | 0.2402 | - | - | id¦99151422¦BAC¦R_5524245¦ | id¦28708345¦BAC¦S_9729721¦
source water1 | Pseudomonas_balearica | 巴利阿里假单胞菌 | 41/4358323 | 0.0009 | 1 | 1 | 1 | Pseudomonas | 假单胞菌属 | 20 | 14 | 1 | 1 | 22 | 15 | G- | 0.27 | 3.46 | 0.0124 | 0.1568 | - | - | id¦28982165¦BAC¦R_9119616¦ | id¦76916168¦BAC¦S_9260501¦
source water1 | Pseudomonas_aeruginosa | 铜绿假单胞菌 | 527/7497593 | 0.007 | 1 | 15 | 0 | Pseudomonas | 假单胞菌属 | 20 | 14 | 16 | 0 | 22 | 15 | G- | 2.39 | 3.46 | 0.1082 | 0.1568 | 1 | 0.96 | id¦94137680¦BAC¦R_2366448¦ | id¦01116727¦BAC¦S_0393240¦
source water1 | Lawsonella_clevelandensis | - | 328/1591018 | 0.0206 | 1 | 8 | 8 | Lawsonella | - | 8 | 8 | 9 | 9 | 9 | 9 | G+ | 6 | 6 | 0.272 | 0.272 | 1 | 0.99 | id¦69293027¦BAC¦R_0738201¦ | id¦18591803¦BAC¦S_9676445¦
source water1 | Caldicellulosiruptor_acetigenus | 产乙酸热解纤维素菌 | 123/2590317 | 0.0047 | 1 | 3 | 1 | Caldicellulosiruptor | 热解纤维素菌属 | 8 | 6 | 3 | 1 | 9 | 6 | G+ | 1.38 | 3.78 | 0.0627 | 0.1714 | - | - | id¦57266958¦BAC¦R_7258166¦ | id¦69708929¦BAC¦S_5914124¦
source water1 | Caldicellulosiruptor_owensensis | 欧文氏热解纤维素菌 | 82/2177425 | 0.0038 | 1 | 2 | 1 | Caldicellulosiruptor | 热解纤维素菌属 | 8 | 6 | 2 | 1 | 9 | 6 | G+ | 1.1 | 3.78 | 0.0497 | 0.1714 | - | - | id¦90943433¦BAC¦R_2816000¦ | id¦19959773¦BAC¦S_9069934¦
source water1 | Moraxella_osloensis | 奥斯陆莫拉菌 | 123/2983035 | 0.0041 | 1 | 6 | 5 | Moraxella | 莫拉菌属 | 6 | 6 | 6 | 5 | 6 | 6 | G- | 2.4 | 2.4 | 0.1088 | 0.1088 | - | - | id¦78445804¦BAC¦R_1006151¦ | id¦03018125¦BAC¦S_5034603¦
source water1 | Staphylococcus_capitis | 头葡萄球菌 | 75/2467666 | 0.003 | 1 | 2 | 1 | Staphylococcus | 葡萄球菌属 | 8 | 6 | 2 | 1 | 9 | 6 | G+ | 0.97 | 3.71 | 0.0438 | 0.1683 | - | - | id¦91254114¦BAC¦R_4675524¦ | id¦78222658¦BAC¦S_6642837¦
source water1 | Staphylococcus_epidermidis | 表皮葡萄球菌 | 41/2573893 | 0.0016 | 1 | 1 | 1 | Staphylococcus | 葡萄球菌属 | 8 | 6 | 1 | 1 | 9 | 6 | G+ | 0.46 | 3.71 | 0.021 | 0.1683 | - | - | id¦79966932¦BAC¦R_5619964¦ | id¦81948656¦BAC¦S_6145183¦
source water1 | Actinomyces_dentalis | 牙齿放线菌 | 41/3530612 | 0.0012 | 1 | 1 | 1 | Actinomyces | 放线菌属 | 5 | 5 | 1 | 1 | 5 | 5 | G+ | 0.34 | 1.86 | 0.0153 | 0.0844 | - | - | id¦69977362¦BAC¦R_7180295¦ | id¦22407282¦BAC¦S_8743862¦
source water1 | Actinomyces_naeslundii | 内氏放线菌 | 41/3228904 | 0.0013 | 1 | 2 | 1 | Actinomyces | 放线菌属 | 5 | 5 | 2 | 1 | 5 | 5 | G+ | 0.74 | 1.86 | 0.0335 | 0.0844 | - | - | id¦68615166¦BAC¦R_2483541¦ | id¦63177970¦BAC¦S_7167271¦
source water1 | Actinomyces_oris | 口腔放线菌 | 41/3042917 | 0.0013 | 1 | 2 | 1 | Actinomyces | 放线菌属 | 5 | 5 | 2 | 1 | 5 | 5 | G+ | 0.78 | 1.86 | 0.0356 | 0.0844 | - | - | id¦03688343¦BAC¦R_5678316¦ | id¦19392096¦BAC¦S_9396489¦
source water1 | Burkholderia_contaminans | 污染伯克霍尔德菌 | 123/8761548 | 0.0014 | 1 | 3 | 1 | Burkholderia | 伯克霍尔德菌属 | 7 | 5 | 3 | 1 | 8 | 5 | G- | 0.41 | 0.96 | 0.0185 | 0.0437 | - | - | id¦08103812¦BAC¦R_8005672¦ | id¦69725635¦BAC¦S_9905471¦
source water1 | Burkholderia_catarinensis | 圣卡塔琳娜州霍尔德菌 | 41/8053896 | 0.0005 | 1 | 1 | 0 | Burkholderia | 伯克霍尔德菌属 | 7 | 5 | 1 | 0 | 8 | 5 | G- | 0.15 | 0.96 | 0.0067 | 0.0437 | - | - | id¦01658404¦BAC¦R_2928415¦ | id¦39079153¦BAC¦S_6266117¦
source water1 | Chryseobacterium_daeguense | 大邱金黄杆菌 | 41/4214660 | 0.001 | 1 | 1 | 1 | Chryseobacterium | 金黄杆菌属 | 7 | 5 | 1 | 1 | 8 | 5 | G- | 0.28 | 2.7 | 0.0128 | 0.1224 | - | - | id¦63066812¦BAC¦R_1905281¦ | id¦18312156¦BAC¦S_1854671¦
source water1 | Chryseobacterium_haifense | 海法金黄杆菌 | 41/2663865 | 0.0015 | 1 | 2 | 1 | Chryseobacterium | 金黄杆菌属 | 7 | 5 | 2 | 1 | 8 | 5 | G- | 0.9 | 2.7 | 0.0406 | 0.1224 | - | - | id¦59086387¦BAC¦R_4304920¦ | id¦30510620¦BAC¦S_1973180¦
source water1 | Chryseobacterium_hominis | 人型金黄杆菌 | 41/2789542 | 0.0015 | 1 | 1 | 1 | Chryseobacterium | 金黄杆菌属 | 7 | 5 | 1 | 1 | 8 | 5 | G- | 0.43 | 2.7 | 0.0194 | 0.1224 | - | - | id¦71525583¦BAC¦R_0824265¦ | id¦54918380¦BAC¦S_5767828¦
source water1 | Chryseobacterium_taklimakanense | 塔拉玛干金黄杆菌 | 41/2538787 | 0.0016 | 1 | 1 | 1 | Chryseobacterium | 金黄杆菌属 | 7 | 5 | 1 | 1 | 8 | 5 | G- | 0.47 | 2.7 | 0.0213 | 0.1224 | - | - | id¦51635248¦BAC¦R_5863417¦ | id¦58889401¦BAC¦S_5928381¦
source water1 | Corynebacterium_minutissimum | 极小棒杆菌 | 41/2696013 | 0.0015 | 1 | 1 | 1 | Corynebacterium | 棒杆菌属 | 8 | 5 | 1 | 1 | 9 | 5 | G+ | 0.44 | 3.79 | 0.0201 | 0.1719 | - | - | id¦77436988¦BAC¦R_8096250¦ | id¦27307884¦BAC¦S_2215806¦
source water1 | Corynebacterium_afermentans | 非发酵棒杆菌 | 41/2236276 | 0.0018 | 1 | 1 | 0 | Corynebacterium | 棒杆菌属 | 8 | 5 | 1 | 0 | 9 | 5 | G+ | 0.53 | 3.79 | 0.0242 | 0.1719 | - | - | id¦55543409¦BAC¦R_3165549¦ | id¦03030659¦BAC¦S_5315763¦
source water1 | Delftia_acidovorans | 食酸代尔夫特菌 | 123/6169231 | 0.002 | 1 | 4 | 0 | Delftia | 代尔夫特菌属 | 5 | 5 | 4 | 0 | 5 | 5 | G- | 0.77 | 0.95 | 0.0351 | 0.0433 | - | - | id¦39884028¦BAC¦R_8614086¦ | id¦25585541¦BAC¦S_9184453¦
source water1 | Delftia_tsuruhatensis | 鶴羽田代尔夫特菌 | 41/6604746 | 0.0006 | 1 | 1 | 0 | Delftia | 代尔夫特菌属 | 5 | 5 | 1 | 0 | 5 | 5 | G- | 0.18 | 0.95 | 0.0082 | 0.0433 | - | - | id¦07980385¦BAC¦R_4686900¦ | id¦77043306¦BAC¦S_7892112¦
source water1 | Pedobacter_caeni | 污水土地杆菌 | 164/7826575 | 0.0021 | 1 | 4 | 4 | Pedobacter | 土地杆菌属 | 5 | 5 | 4 | 4 | 5 | 5 | G- | 0.61 | 0.76 | 0.0277 | 0.0344 | 1 | 0.51 | id¦19020654¦BAC¦R_5929241¦ | id¦72247450¦BAC¦S_7555586¦
source water1 | Pedobacter_steynii | 斯氏土地杆菌 | 41/8068308 | 0.0005 | 1 | 1 | 1 | Pedobacter | 土地杆菌属 | 5 | 5 | 1 | 1 | 5 | 5 | G- | 0.15 | 0.76 | 0.0067 | 0.0344 | - | - | id¦10625996¦BAC¦R_6408309¦ | id¦98036895¦BAC¦S_7956901¦
source water1 | Ralstonia_pickettii | 皮氏罗尔斯顿菌 | 205/4971055 | 0.0041 | 1 | 5 | 4 | Ralstonia | 罗尔斯顿菌属 | 6 | 5 | 5 | 4 | 6 | 5 | G- | 1.2 | 1.39 | 0.0544 | 0.063 | 1 | 0.96 | id¦34113688¦BAC¦R_2898822¦ | id¦99940213¦BAC¦S_3917488¦
source water1 | Ralstonia_insidiosa | 危险罗尔斯顿菌 | 41/6316094 | 0.0006 | 1 | 1 | 0 | Ralstonia | 罗尔斯顿菌属 | 6 | 5 | 1 | 0 | 6 | 5 | G- | 0.19 | 1.39 | 0.0086 | 0.063 | - | - | id¦47371922¦BAC¦R_7451528¦ | id¦44746198¦BAC¦S_8470464¦
source water1 | Aeribacillus_composti | 堆肥气芽胞杆菌 | 41/3778206 | 0.0011 | 1 | 1 | 0 | Aeribacillus | 气芽胞杆菌属 | 4 | 4 | 1 | 0 | 4 | 4 | G+ | 0.32 | 1.25 | 0.0143 | 0.0567 | - | - | id¦02898183¦BAC¦R_8307278¦ | id¦36857853¦BAC¦S_4458063¦
source water1 | Aeribacillus_pallidus | 苍白气芽胞杆菌 | 82/3824810 | 0.0021 | 1 | 3 | 0 | Aeribacillus | 气芽胞杆菌属 | 4 | 4 | 3 | 0 | 4 | 4 | G+ | 0.93 | 1.25 | 0.0424 | 0.0567 | - | - | id¦71580521¦BAC¦R_2718758¦ | id¦07071783¦BAC¦S_5381751¦
source water1 | Bradyrhizobium_sp._BTAi1 | 慢生根瘤菌BTAi1 | 82/8264687 | 0.001 | 1 | 2 | 1 | Bradyrhizobium | 慢生根瘤菌属 | 20 | 4 | 2 | 1 | 22 | 4 | G- | 0.29 | 2.83 | 0.0131 | 0.1286 | - | - | id¦39765305¦BAC¦R_9966658¦ | id¦83252480¦BAC¦S_8337294¦
source water1 | Bradyrhizobium_cosmicum | 遍生慢生根瘤菌 | 41/7304136 | 0.0006 | 1 | 1 | 0 | Bradyrhizobium | 慢生根瘤菌属 | 20 | 4 | 1 | 0 | 22 | 4 | G- | 0.16 | 2.83 | 0.0074 | 0.1286 | - | - | id¦49451420¦BAC¦R_3926832¦ | id¦99126259¦BAC¦S_7108697¦
source water1 | Micrococcus_endophyticus | 植物内生微球菌 | 82/1100928 | 0.0074 | 1 | 2 | 1 | Micrococcus | 微球菌属 | 6 | 4 | 2 | 1 | 6 | 4 | G+ | 2.17 | 3.99 | 0.0983 | 0.1812 | - | - | id¦32544843¦BAC¦R_0182842¦ | id¦88860031¦BAC¦S_9344633¦
source water1 | Micrococcus_terreus | 土微球菌 | 41/3087820 | 0.0013 | 1 | 1 | 1 | Micrococcus | 微球菌属 | 6 | 4 | 1 | 1 | 6 | 4 | G+ | 0.39 | 3.99 | 0.0175 | 0.1812 | - | - | id¦58203890¦BAC¦R_2437942¦ | id¦66191775¦BAC¦S_0069957¦
source water1 | Rhodococcus_fascians | 束红球菌 | 41/5967106 | 0.0007 | 1 | 1 | 1 | Rhodococcus | 红球菌属 | 4 | 4 | 1 | 1 | 4 | 4 | G+ | 0.2 | 0.75 | 0.0091 | 0.034 | - | - | id¦23448916¦BAC¦R_0336836¦ | id¦12406773¦BAC¦S_0484691¦
source water1 | Rhodococcus_enclensis | 印度国化室红球菌?? | 41/7478043 | 0.0005 | 1 | 1 | 0 | Rhodococcus | 红球菌属 | 4 | 4 | 1 | 0 | 4 | 4 | G+ | 0.16 | 0.75 | 0.0072 | 0.034 | - | - | id¦78839942¦BAC¦R_5954881¦ | id¦98901954¦BAC¦S_7747985¦
source water1 | Acidovorax_carolinensis | 北卡罗来纳食酸菌 | 123/4077847 | 0.003 | 1 | 3 | 1 | Acidovorax | 食酸菌属 | 8 | 3 | 3 | 1 | 9 | 3 | G- | 0.88 | 2.23 | 0.0398 | 0.1013 | - | - | id¦99809340¦BAC¦R_9685281¦ | id¦23151307¦BAC¦S_0024136¦
source water1 | Acidovorax_temperans | 温和食酸菌 | 123/4651444 | 0.0026 | 1 | 3 | 1 | Acidovorax | 食酸菌属 | 8 | 3 | 3 | 1 | 9 | 3 | G- | 0.77 | 2.23 | 0.0349 | 0.1013 | - | - | id¦02810628¦BAC¦R_8344044¦ | id¦27147656¦BAC¦S_4831994¦
source water1 | Caulobacter_vibrioides | 弧形柄杆菌 | 82/4123726 | 0.002 | 1 | 3 | 1 | Caulobacter | 柄杆菌属 | 6 | 3 | 3 | 1 | 6 | 3 | G- | 0.87 | 1.6 | 0.0394 | 0.0724 | - | - | id¦98034742¦BAC¦R_7356619¦ | id¦03591998¦BAC¦S_6058582¦
source water1 | Caulobacter_flavus | 黄色柄杆菌 | 41/5659202 | 0.0007 | 1 | 1 | 0 | Caulobacter | 柄杆菌属 | 6 | 3 | 1 | 0 | 6 | 3 | G- | 0.21 | 1.6 | 0.0096 | 0.0724 | - | - | id¦85954764¦BAC¦R_3631900¦ | id¦46087306¦BAC¦S_8880942¦
source water1 | Janibacter_anophelis | 按蚊中肠两面神菌 | 41/3433193 | 0.0012 | 1 | 1 | 1 | Janibacter | 两面神菌属 | 3 | 3 | 1 | 1 | 3 | 3 | G+ | 0.35 | 1.07 | 0.0158 | 0.0484 | - | - | id¦27950644¦BAC¦R_8402515¦ | id¦71032871¦BAC¦S_7051218¦
source water1 | Janibacter_hoylei | 霍伊尔两面神菌 | 41/3134151 | 0.0013 | 1 | 1 | 1 | Janibacter | 两面神菌属 | 3 | 3 | 1 | 1 | 3 | 3 | G+ | 0.38 | 1.07 | 0.0173 | 0.0484 | - | - | id¦63479072¦BAC¦R_7127218¦ | id¦89291528¦BAC¦S_1018326¦
source water1 | Aquabacterium_olei | 油水小杆菌 | 123/3890087 | 0.0032 | 1 | 3 | 1 | Aquabacterium | 水小杆菌属 | 3 | 2 | 3 | 1 | 3 | 2 | G- | 0.92 | 0.92 | 0.0417 | 0.0417 | - | - | id¦82117975¦BAC¦R_1965251¦ | id¦99573920¦BAC¦S_3278383¦
source water1 | Bacillus_paralicheniformis | 副地衣芽胞杆菌 | 41/4541365 | 0.0009 | 1 | 1 | 1 | Bacillus | 芽胞杆菌属 | 2 | 2 | 1 | 1 | 2 | 2 | G+ | 0.26 | 0.51 | 0.0119 | 0.0233 | - | - | id¦57694848¦BAC¦R_9466172¦ | id¦44008393¦BAC¦S_8956300¦
source water1 | Bacillus_licheniformis | 地衣芽胞杆菌 | 41/4731903 | 0.0009 | 1 | 1 | 0 | Bacillus | 芽胞杆菌属 | 2 | 2 | 1 | 0 | 2 | 2 | G+ | 0.25 | 0.51 | 0.0114 | 0.0233 | - | - | id¦83700957¦BAC¦R_7057621¦ | id¦11773467¦BAC¦S_7708432¦
source water1 | Brachybacterium_alimentarium | 食物小短杆菌 | 41/4263269 | 0.001 | 1 | 1 | 1 | Brachybacterium | 小短杆菌属 | 3 | 2 | 1 | 1 | 3 | 2 | G+ | 0.28 | 0.94 | 0.0127 | 0.0425 | - | - | id¦13350663¦BAC¦R_2488667¦ | id¦71762648¦BAC¦S_1563019¦
source water1 | Brachybacterium_faecium | 粪小短杆菌 | 41/3531134 | 0.0012 | 1 | 1 | 0 | Brachybacterium | 小短杆菌属 | 3 | 2 | 1 | 0 | 3 | 2 | G+ | 0.34 | 0.94 | 0.0153 | 0.0425 | - | - | id¦95513167¦BAC¦R_1112639¦ | id¦29265745¦BAC¦S_0264121¦
source water1 | Enterococcus_cecorum | 盲肠肠球菌 | 82/2273393 | 0.0036 | 1 | 2 | 2 | Enterococcus | 肠球菌属 | 2 | 2 | 2 | 2 | 2 | 2 | G+ | 1.05 | 1.05 | 0.0476 | 0.0476 | - | - | id¦30622239¦BAC¦R_8293228¦ | id¦23097671¦BAC¦S_8975236¦
source water1 | Finegoldia_magna | 大芬戈尔德菌 | 41/1757245 | 0.0023 | 1 | 2 | 2 | Finegoldia | 芬戈尔德菌属 | 2 | 2 | 2 | 2 | 2 | 2 | G+ | 1.36 | 1.36 | 0.0616 | 0.0616 | - | - | id¦05322651¦BAC¦R_1628165¦ | id¦96027472¦BAC¦S_9699449¦
source water1 | Haemophilus_parainfluenzae | 副流感嗜血杆菌 | 41/2067650 | 0.002 | 1 | 2 | 1 | Haemophilus | 嗜血杆菌属 | 2 | 2 | 2 | 1 | 2 | 2 | G- | 1.15 | 1.15 | 0.0523 | 0.0523 | - | - | id¦15869544¦BAC¦R_6266463¦ | id¦77177367¦BAC¦S_3784721¦
source water1 | Lactococcus_lactis | 乳酸乳球菌 | 81/2961275 | 0.0027 | 1 | 2 | 2 | Lactococcus | 乳球菌属 | 2 | 2 | 2 | 2 | 2 | 2 | G+ | 0.8 | 0.8 | 0.0365 | 0.0365 | - | - | id¦78619619¦BAC¦R_2385314¦ | id¦68242179¦BAC¦S_5224148¦
source water1 | Lentibacillus_salicampi | 盐田慢生芽胞杆菌 | 82/3884006 | 0.0021 | 1 | 2 | 2 | Lentibacillus | 慢生芽胞杆菌属 | 2 | 2 | 2 | 2 | 2 | 2 | Gram-variable | 0.62 | 0.62 | 0.0279 | 0.0279 | - | - | id¦84883831¦BAC¦R_7329837¦ | id¦00357482¦BAC¦S_1351270¦
source water1 | Methyloversatilis_universalis | - | 82/4227249 | 0.0019 | 1 | 2 | 1 | Methyloversatilis | - | 2 | 2 | 2 | 1 | 2 | 2 | G- | 0.56 | 0.56 | 0.0256 | 0.0256 | - | - | id¦83734465¦BAC¦R_1463558¦ | id¦40045076¦BAC¦S_3332999¦
source water1 | Mycolicibacterium_arabiense | 阿拉伯分枝杆菌 | 82/6017160 | 0.0014 | 1 | 2 | 0 | Mycolicibacterium | - | 3 | 2 | 2 | 0 | 3 | 2 | G+ | 0.4 | 0.59 | 0.018 | 0.0268 | - | - | id¦69145085¦BAC¦R_7121668¦ | id¦90630660¦BAC¦S_9105057¦
source water1 | Mycolicibacterium_tusciae | 托斯卡分枝杆菌 | 41/6157473 | 0.0007 | 1 | 1 | 0 | Mycolicibacterium | - | 3 | 2 | 1 | 0 | 3 | 2 | G+ | 0.19 | 0.59 | 0.0088 | 0.0268 | - | - | id¦14751492¦BAC¦R_1781272¦ | id¦23673968¦BAC¦S_5652400¦
source water1 | Sphingobacterium_lactis | 乳鞘氨醇杆菌 | 41/4030188 | 0.001 | 1 | 1 | 1 | Sphingobacterium | 鞘氨醇杆菌属 | 2 | 2 | 1 | 1 | 2 | 2 | G- | 0.3 | 0.49 | 0.0134 | 0.0224 | - | - | id¦25930705¦BAC¦R_8138950¦ | id¦11271582¦BAC¦S_7600134¦
source water1 | Sphingobacterium_multivorum | 多食鞘氨醇杆菌 | 41/5984996 | 0.0007 | 1 | 1 | 1 | Sphingobacterium | 鞘氨醇杆菌属 | 2 | 2 | 1 | 1 | 2 | 2 | G- | 0.2 | 0.49 | 0.009 | 0.0224 | - | - | id¦32625785¦BAC¦R_0844755¦ | id¦04755840¦BAC¦S_5848964¦
source water1 | Sphingomonas_melonis | 甜瓜鞘氨醇单胞菌 | 41/3942577 | 0.001 | 1 | 1 | 0 | Sphingomonas | 鞘氨醇单胞菌属 | 3 | 2 | 1 | 0 | 3 | 2 | G- | 0.3 | 0.87 | 0.0137 | 0.0393 | - | - | id¦12709173¦BAC¦R_8349368¦ | id¦23570126¦BAC¦S_5825886¦
source water1 | Sphingomonas_paucimobilis | 少动鞘氨醇单胞菌 | 41/4005505 | 0.001 | 1 | 1 | 0 | Sphingomonas | 鞘氨醇单胞菌属 | 3 | 2 | 1 | 0 | 3 | 2 | G- | 0.3 | 0.87 | 0.0135 | 0.0393 | - | - | id¦72686424¦BAC¦R_4428915¦ | id¦49350332¦BAC¦S_4242188¦
source water1 | Streptococcus_oralis | 口腔链球菌 | 41/1872903 | 0.0022 | 1 | 1 | 1 | Streptococcus | 链球菌属 | 2 | 2 | 1 | 1 | 2 | 2 | G+ | 0.64 | 1.23 | 0.0289 | 0.0559 | - | - | id¦66920924¦BAC¦R_4690967¦ | id¦41327418¦BAC¦S_7770086¦
source water1 | Streptococcus_mitis | 缓症链球菌 | 41/2005729 | 0.002 | 1 | 1 | 0 | Streptococcus | 链球菌属 | 2 | 2 | 1 | 0 | 2 | 2 | G+ | 0.6 | 1.23 | 0.027 | 0.0559 | - | - | id¦89924070¦BAC¦R_7367586¦ | id¦71856117¦BAC¦S_5870034¦
source water1 | Thermus_parvatiensis | 栖热菌* | 36/2036760 | 0.0018 | 1 | 1 | 0 | Thermus | 栖热菌属 | 3 | 2 | 1 | 0 | 3 | 2 | G- | 0.59 | 1.71 | 0.0266 | 0.0775 | - | - | id¦56431089¦BAC¦R_9958079¦ | id¦02439826¦BAC¦S_8995787¦
source water1 | Thermus_scotoductus | 水管致黑栖热菌 | 38/2363025 | 0.0016 | 1 | 1 | 0 | Thermus | 栖热菌属 | 3 | 2 | 1 | 0 | 3 | 2 | G- | 0.5 | 1.71 | 0.0229 | 0.0775 | - | - | id¦73472961¦BAC¦R_7815903¦ | id¦62537656¦BAC¦S_4433354¦
source water1 | Acetobacter_orientalis | 东方醋杆菌 | 41/3041114 | 0.0013 | 1 | 1 | 1 | Acetobacter | 醋杆菌属 | 3 | 1 | 1 | 1 | 3 | 1 | G- | 0.39 | 1.13 | 0.0178 | 0.0513 | - | - | id¦19568703¦BAC¦R_0333758¦ | id¦92742917¦BAC¦S_2078064¦
source water1 | Acetobacter_peroxydans | 过氧化醋杆菌 | 41/2710317 | 0.0015 | 1 | 1 | 0 | Acetobacter | 醋杆菌属 | 3 | 1 | 1 | 0 | 3 | 1 | G- | 0.44 | 1.13 | 0.02 | 0.0513 | - | - | id¦38442565¦BAC¦R_3654083¦ | id¦29386222¦BAC¦S_1252362¦
source water1 | Altererythrobacter_troitsensis | 特罗伊察交替赤杆菌 | 41/2902347 | 0.0014 | 1 | 1 | 1 | Altererythrobacter | 交替赤杆菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.41 | 0.41 | 0.0186 | 0.0186 | - | - | id¦77286955¦BAC¦R_5001263¦ | id¦53478966¦BAC¦S_1976584¦
source water1 | Bacteroides_thetaiotaomicron | 多形拟杆菌 | 41/6521422 | 0.0006 | 1 | 1 | 0 | Bacteroides | 拟杆菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.18 | 0.18 | 0.0083 | 0.0083 | - | - | id¦54979416¦BAC¦R_6757910¦ | id¦36308058¦BAC¦S_1899560¦
source water1 | Bosea_sp._FBZP-16 | - | 41/6075089 | 0.0007 | 1 | 1 | 1 | Bosea | - | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.2 | 0.2 | 0.0089 | 0.0089 | - | - | id¦23062225¦BAC¦R_6149689¦ | id¦39939772¦BAC¦S_2867792¦
source water1 | Brevundimonas_mediterranea | 地中海短波单胞菌 | 37/3659826 | 0.001 | 1 | 1 | 0 | Brevundimonas | 短波单胞菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.33 | 0.33 | 0.0148 | 0.0148 | - | - | id¦03457104¦BAC¦R_6877505¦ | id¦37886324¦BAC¦S_9963801¦
source water1 | Carboxydocella_sporoproducens | - | 41/2579744 | 0.0016 | 1 | 1 | 0 | Carboxydocella | - | 1 | 1 | 1 | 0 | 1 | 1 | G+ | 0.46 | 0.46 | 0.021 | 0.021 | - | - | id¦50980074¦BAC¦R_1547505¦ | id¦02123824¦BAC¦S_0730841¦
source water1 | Cedecea_lapagei | 拉帕西地西菌 | 41/4778444 | 0.0009 | 1 | 1 | 0 | Cedecea | 西地西菌属 | 6 | 1 | 1 | 0 | 6 | 1 | G- | 0.25 | 1.53 | 0.0113 | 0.0694 | - | - | id¦76373265¦BAC¦R_2182340¦ | id¦82324835¦BAC¦S_1383020¦
source water1 | Cedecea_neteri | 耐特西地西菌 | 164/4659311 | 0.0035 | 1 | 5 | 0 | Cedecea | 西地西菌属 | 6 | 1 | 5 | 0 | 6 | 1 | G- | 1.28 | 1.53 | 0.0581 | 0.0694 | 1 | 0.51 | id¦13870026¦BAC¦R_3246025¦ | id¦69498756¦BAC¦S_0399247¦
source water1 | Citrobacter_youngae | 杨氏柠檬酸杆菌 | 41/4945156 | 0.0008 | 1 | 1 | 0 | Citrobacter | 柠檬酸杆菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.24 | 0.24 | 0.0109 | 0.0109 | - | - | id¦93868117¦BAC¦R_6922119¦ | id¦88056852¦BAC¦S_4957802¦
source water1 | Cloacibacterium_normanense | - | 82/2841437 | 0.0029 | 1 | 2 | 1 | Cloacibacterium | - | 2 | 1 | 2 | 1 | 2 | 1 | G- | 0.84 | 0.84 | 0.0381 | 0.0381 | - | - | id¦05920139¦BAC¦R_4002635¦ | id¦36590735¦BAC¦S_8513847¦
source water1 | Cupriavidus_gilardii | 吉拉迪贪铜菌 | 41/5535252 | 0.0007 | 1 | 1 | 1 | Cupriavidus | 贪铜菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.22 | 0.22 | 0.0098 | 0.0098 | - | - | id¦17628455¦BAC¦R_5168304¦ | id¦74989045¦BAC¦S_8863800¦
source water1 | Devosia_limi | 污水德沃斯菌 | 37/4432477 | 0.0008 | 1 | 1 | 0 | Devosia | 德沃斯菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.27 | 0.27 | 0.0122 | 0.0122 | - | - | id¦19056191¦BAC¦R_9471982¦ | id¦84322935¦BAC¦S_9595191¦
source water1 | Dietzia_alimentaria | 食物迪茨菌 | 41/3718103 | 0.0011 | 1 | 1 | 0 | Dietzia | 迪茨菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G+ | 0.32 | 0.32 | 0.0146 | 0.0146 | - | - | id¦04192415¦BAC¦R_8709485¦ | id¦16173681¦BAC¦S_4199892¦
source water1 | [Clostridium]_innocuum | 无害梭菌 | 41/4836337 | 0.0008 | 1 | 1 | 1 | Erysipelatoclostridium | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.25 | 0.25 | 0.0112 | 0.0112 | - | - | id¦63977131¦BAC¦R_2480764¦ | id¦36116389¦BAC¦S_1497689¦
source water1 | Garciella_nitratireducens | - | 38/2263208 | 0.0017 | 1 | 1 | 1 | Garciella | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.53 | 0.53 | 0.0239 | 0.0239 | - | - | id¦65670347¦BAC¦R_7119058¦ | id¦24158225¦BAC¦S_7560566¦
source water1 | Jeotgalicoccus_halophilus | 嗜盐咸海鲜球菌 | 41/2275506 | 0.0018 | 1 | 1 | 1 | Jeotgalicoccus | 咸海鲜球菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.52 | 0.52 | 0.0238 | 0.0238 | - | - | id¦13643792¦BAC¦R_7812111¦ | id¦38580153¦BAC¦S_1971571¦
source water1 | Kocuria_palustris | 沼泽库克菌 | 41/2854447 | 0.0014 | 1 | 1 | 1 | Kocuria | 库克菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.42 | 0.42 | 0.019 | 0.019 | - | - | id¦31043630¦BAC¦R_5863717¦ | id¦65461644¦BAC¦S_9118994¦
source water1 | Lactobacillus_rossiae | 罗西氏乳杆菌 | 41/2762250 | 0.0015 | 1 | 1 | 1 | Lactobacillus | 乳杆菌属 | 2 | 1 | 1 | 1 | 2 | 1 | G+ | 0.43 | 0.77 | 0.0196 | 0.0348 | - | - | id¦48711661¦BAC¦R_2231919¦ | id¦85465107¦BAC¦S_4677617¦
source water1 | Lactobacillus_pentosus | 戊糖乳杆菌 | 35/3564857 | 0.001 | 1 | 1 | 0 | Lactobacillus | 乳杆菌属 | 2 | 1 | 1 | 0 | 2 | 1 | G+ | 0.34 | 0.77 | 0.0152 | 0.0348 | - | - | id¦65289977¦BAC¦R_3277879¦ | id¦72321128¦BAC¦S_7884414¦
source water1 | Marinitenerispora_sediminis | - | 38/5978284 | 0.0006 | 1 | 1 | 1 | Marinitenerispora | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.2 | 0.2 | 0.009 | 0.009 | - | - | id¦19877324¦BAC¦R_8908472¦ | id¦69456564¦BAC¦S_8416412¦
source water1 | [Ruminococcus]_torques | - | 41/3001723 | 0.0014 | 1 | 1 | 1 | Mediterraneibacter | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.4 | 0.4 | 0.018 | 0.018 | - | - | id¦59364674¦BAC¦R_5470177¦ | id¦86280742¦BAC¦S_8704713¦
source water1 | Meiothermus_silvanus | 森林亚栖热菌 | 41/3249394 | 0.0013 | 1 | 1 | 1 | Meiothermus | 亚栖热菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.37 | 0.37 | 0.0166 | 0.0166 | - | - | id¦38072918¦BAC¦R_5433606¦ | id¦27760635¦BAC¦S_9719475¦
source water1 | Methanothermobacter_thermautotrophicus | 热自养甲烷热杆菌 | 37/1751377 | 0.0021 | 1 | 1 | 1 | Methanothermobacter | 甲烷热杆菌属 | 1 | 1 | 1 | 1 | 1 | 1 | Archaea | 0.68 | 0.68 | 0.0309 | 0.0309 | - | - | id¦20116691¦BAC¦R_4798506¦ | id¦80371143¦BAC¦S_9149878¦
source water1 | Neisseria_flavescens | 浅黄奈瑟菌 | 41/2250253 | 0.0018 | 1 | 1 | 0 | Neisseria | 奈瑟菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.53 | 0.53 | 0.024 | 0.024 | - | - | id¦19135610¦BAC¦R_7481958¦ | id¦02704742¦BAC¦S_3424993¦
source water1 | Nocardioides_daejeonensis | 大田类诺卡菌 | 41/4400905 | 0.0009 | 1 | 1 | 1 | Nocardioides | 类诺卡菌属 | 2 | 1 | 1 | 1 | 2 | 1 | G+ | 0.27 | 0.52 | 0.0123 | 0.0235 | - | - | id¦94955028¦BAC¦R_6448379¦ | id¦93841680¦BAC¦S_4505906¦
source water1 | Nocardioides_rubriscoriae | 火山灰类诺卡菌 | 41/4827517 | 0.0008 | 1 | 1 | 0 | Nocardioides | 类诺卡菌属 | 2 | 1 | 1 | 0 | 2 | 1 | G+ | 0.25 | 0.52 | 0.0112 | 0.0235 | - | - | id¦67074635¦BAC¦R_0068548¦ | id¦12150441¦BAC¦S_1012970¦
source water1 | Ochrobactrum_haematophilum | 嗜血苍白杆菌 | 41/5548106 | 0.0007 | 1 | 1 | 1 | Ochrobactrum | 苍白杆菌属 | 2 | 1 | 1 | 1 | 2 | 1 | G- | 0.22 | 0.44 | 0.0098 | 0.0201 | - | - | id¦77084125¦BAC¦R_2782562¦ | id¦35256811¦BAC¦S_6779643¦
source water1 | Ochrobactrum_pecoris | 牲畜苍白杆菌 | 41/5238803 | 0.0008 | 1 | 1 | 0 | Ochrobactrum | 苍白杆菌属 | 2 | 1 | 1 | 0 | 2 | 1 | G- | 0.23 | 0.44 | 0.0103 | 0.0201 | - | - | id¦88199296¦BAC¦R_9104165¦ | id¦99047965¦BAC¦S_6747851¦
source water1 | Paenibacillus_taichungensis | 台中类芽胞杆菌 | 41/6980167 | 0.0006 | 1 | 1 | 0 | Paenibacillus | 类芽胞杆菌属 | 1 | 1 | 1 | 0 | 1 | 1 | Gram-variable | 0.17 | 0.17 | 0.0078 | 0.0078 | - | - | id¦69420407¦BAC¦R_0037778¦ | id¦03287722¦BAC¦S_4435183¦
source water1 | Paraburkholderia_bannensis | 班纳副伯克霍尔德菌 | 41/7195551 | 0.0006 | 1 | 1 | 0 | Paraburkholderia | 副伯克霍尔德菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.17 | 0.17 | 0.0075 | 0.0075 | - | - | id¦81955139¦BAC¦R_9014626¦ | id¦33265089¦BAC¦S_7868844¦
source water1 | Parvimonas_micra | 微小微单胞菌 | 41/1631761 | 0.0025 | 1 | 1 | 1 | Parvimonas | 微单胞菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.73 | 0.73 | 0.0332 | 0.0332 | - | - | id¦09880509¦BAC¦R_4373556¦ | id¦97218525¦BAC¦S_0104274¦
source water1 | Pluralibacter_gergoviae | 日勾维多源杆菌 | 82/5654065 | 0.0015 | 1 | 2 | 1 | Pluralibacter | 多源杆菌属 | 2 | 1 | 2 | 1 | 2 | 1 | G- | 0.42 | 0.42 | 0.0191 | 0.0191 | - | - | id¦89208193¦BAC¦R_3529103¦ | id¦01873914¦BAC¦S_7273219¦
source water1 | Pseudarthrobacter_phenanthrenivorans | 嗜菲假节杆菌 | 41/4316569 | 0.0009 | 1 | 1 | 1 | Pseudarthrobacter | 假节杆菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.28 | 0.28 | 0.0125 | 0.0125 | - | - | id¦56647498¦BAC¦R_0218579¦ | id¦61836805¦BAC¦S_9365495¦
source water1 | Reyranella_soli | - | 41/9822188 | 0.0004 | 1 | 1 | 0 | Reyranella | - | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.12 | 0.12 | 0.0055 | 0.0055 | - | - | id¦50328797¦BAC¦R_4386186¦ | id¦63520749¦BAC¦S_9002388¦
source water1 | Rhizobium_pusense | 普萨根瘤菌 | 41/5285620 | 0.0008 | 1 | 1 | 1 | Rhizobium | 根瘤菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.22 | 0.22 | 0.0102 | 0.0102 | - | - | id¦43384912¦BAC¦R_6112086¦ | id¦54701733¦BAC¦S_2580134¦
source water1 | Rothia_mucilaginosa | 黏液罗氏菌 | 41/2253579 | 0.0018 | 1 | 1 | 1 | Rothia | 罗氏菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.53 | 0.53 | 0.024 | 0.024 | - | - | id¦11637400¦BAC¦R_8187461¦ | id¦64873621¦BAC¦S_0860975¦
source water1 | Sanguibacter_keddieii | 科氏血杆菌 | 41/2352760 | 0.0017 | 1 | 1 | 1 | Sanguibacter | 血杆菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.51 | 0.51 | 0.023 | 0.023 | - | - | id¦43012025¦BAC¦R_2392898¦ | id¦53530719¦BAC¦S_9806900¦
source water1 | Serratia_marcescens | 黏质沙雷菌 | 41/5429004 | 0.0008 | 1 | 1 | 1 | Serratia | 沙雷菌属 | 2 | 1 | 1 | 1 | 2 | 1 | G- | 0.22 | 0.45 | 0.01 | 0.0205 | - | - | id¦68740260¦BAC¦R_4309087¦ | id¦90467460¦BAC¦S_4152514¦
source water1 | Serratia_rubidaea | 深红沙雷菌 | 41/5172175 | 0.0008 | 1 | 1 | 0 | Serratia | 沙雷菌属 | 2 | 1 | 1 | 0 | 2 | 1 | G- | 0.23 | 0.45 | 0.0105 | 0.0205 | - | - | id¦51433965¦BAC¦R_5112350¦ | id¦27809695¦BAC¦S_7014392¦
source water1 | Sphingobium_yanoikuyae | 矢野口鞘脂菌 | 41/4932428 | 0.0008 | 1 | 1 | 1 | Sphingobium | 鞘脂菌属 | 2 | 1 | 1 | 1 | 2 | 1 | G- | 0.24 | 0.51 | 0.011 | 0.023 | - | - | id¦65433060¦BAC¦R_9762423¦ | id¦75042391¦BAC¦S_3739105¦
source water1 | Sphingobium_estronivorans | 食雌激素酮鞘脂菌 | 37/4502394 | 0.0008 | 1 | 1 | 0 | Sphingobium | 鞘脂菌属 | 2 | 1 | 1 | 0 | 2 | 1 | G- | 0.26 | 0.51 | 0.012 | 0.023 | - | - | id¦77567163¦BAC¦R_3279257¦ | id¦84105953¦BAC¦S_2888873¦
source water1 | Tetzosporium_hominis | - | 41/2687030 | 0.0015 | 1 | 1 | 1 | Tetzosporium | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.44 | 0.44 | 0.0201 | 0.0201 | - | - | id¦14362774¦BAC¦R_0158627¦ | id¦10030208¦BAC¦S_6441909¦
source water1 | Veillonella_atypica | 非典型韦荣球菌 | 41/2108012 | 0.0019 | 1 | 1 | 1 | Veillonella | 韦荣球菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.57 | 0.57 | 0.0257 | 0.0257 | - | - | id¦16888080¦BAC¦R_9289936¦ | id¦89315361¦BAC¦S_5539862¦
source water1 | Yimella_lutea | - | 41/3533116 | 0.0012 | 1 | 1 | 1 | Yimella | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.34 | 0.34 | 0.0153 | 0.0153 | - | - | id¦59591354¦BAC¦R_8973304¦ | id¦11089479¦BAC¦S_8817654¦
source water 2 | Cutibacterium_granulosum | - | 294/2175244 | 0.0135 | 1 | 7 | 6 | Cutibacterium | - | 633 | 575 | 3 | 2 | 234 | 212 | G+ | 0.2 | 14.67 | 0.0594 | 4.2587 | 1 | 0.62 | id¦77522930¦BAC¦R_0272957¦ | id¦05220705¦BAC¦S_7001618¦
source water 2 | Methyloversatilis_thermotolerans | - | 496/4160889 | 0.0119 | 1 | 12 | 1 | Methyloversatilis | - | 737 | 510 | 4 | 1 | 272 | 188 | G- | 0.18 | 11.03 | 0.0532 | 3.2017 | 1 | 0.92 | id¦67645595¦BAC¦R_6039988¦ | id¦03758844¦BAC¦S_1200795¦
source water 2 | Pseudomonas_alcaligenes | 产碱假单胞菌 | 336/5016493 | 0.0067 | 1 | 13 | 7 | Pseudomonas | 假单胞菌属 | 364 | 257 | 5 | 3 | 134 | 95 | G- | 0.16 | 3.79 | 0.0478 | 1.1009 | 1 | 0.99 | id¦01730270¦BAC¦R_4673067¦ | id¦73667852¦BAC¦S_3353884¦
source water 2 | Pseudomonas_simiae | 猴假单胞菌 | 840/6168122 | 0.0136 | 1 | 20 | 7 | Pseudomonas | 假单胞菌属 | 364 | 257 | 7 | 3 | 134 | 95 | G- | 0.21 | 3.79 | 0.0598 | 1.1009 | 1 | 0.95 | id¦31336011¦BAC¦R_7736582¦ | id¦27062128¦BAC¦S_5471689¦
source water 2 | Pseudomonas_aeruginosa | 铜绿假单胞菌 | 2619/7564383 | 0.0346 | 1 | 77 | 5 | Pseudomonas | 假单胞菌属 | 364 | 257 | 28 | 2 | 134 | 95 | G- | 0.65 | 3.79 | 0.1878 | 1.1009 | 1 | 0.9 | id¦39866963¦BAC¦R_2319190¦ | id¦01116727¦BAC¦S_0393240¦
source water 2 | Pseudomonas_peli | 烂泥假单胞菌 | 828/4508359 | 0.0184 | 1 | 20 | 5 | Pseudomonas | 假单胞菌属 | 364 | 257 | 7 | 2 | 134 | 95 | G- | 0.28 | 3.79 | 0.0819 | 1.1009 | 1 | 0.98 | id¦11862698¦BAC¦R_3598212¦ | id¦72598654¦BAC¦S_5314334¦
source water 2 | Pseudomonas_anguilliseptica | 鳗败血假单胞菌 | 462/5229637 | 0.0088 | 1 | 11 | 4 | Pseudomonas | 假单胞菌属 | 364 | 257 | 4 | 1 | 134 | 95 | G- | 0.13 | 3.79 | 0.0388 | 1.1009 | 1 | 0.99 | id¦96934681¦BAC¦R_1865571¦ | id¦62109121¦BAC¦S_6085391¦
source water 2 | Pseudomonas_moraviensis | 摩拉维亚假单胞菌 | 126/6134490 | 0.0021 | 1 | 4 | 3 | Pseudomonas | 假单胞菌属 | 364 | 257 | 1 | 1 | 134 | 95 | G- | 0.04 | 3.79 | 0.012 | 1.1009 | - | - | id¦35950925¦BAC¦R_7619003¦ | id¦85980360¦BAC¦S_4334564¦
source water 2 | Pseudomonas_protegens | 保护假单胞菌 | 82/7087572 | 0.0012 | 1 | 3 | 2 | Pseudomonas | 假单胞菌属 | 364 | 257 | 1 | 1 | 134 | 95 | G- | 0.03 | 3.79 | 0.0078 | 1.1009 | - | - | id¦18172438¦BAC¦R_8063316¦ | id¦71830054¦BAC¦S_7782925¦
source water 2 | Pseudomonas_yamanorum | 亚玛那假单胞菌 | 84/7183454 | 0.0012 | 1 | 3 | 2 | Pseudomonas | 假单胞菌属 | 364 | 257 | 1 | 1 | 134 | 95 | G- | 0.03 | 3.79 | 0.0077 | 1.1009 | - | - | id¦27402613¦BAC¦R_4126261¦ | id¦97715640¦BAC¦S_0539357¦
source water 2 | Pseudomonas_alcaliphila | 嗜碱假单胞菌 | 294/5340293 | 0.0055 | 1 | 9 | 1 | Pseudomonas | 假单胞菌属 | 364 | 257 | 3 | 1 | 134 | 95 | G- | 0.11 | 3.79 | 0.0311 | 1.1009 | 1 | 0.72 | id¦74570986¦BAC¦R_5740609¦ | id¦14183881¦BAC¦S_4590602¦
source water 2 | Pseudomonas_asiatica | 亚洲假单胞菌 | 42/6143444 | 0.0007 | 1 | 3 | 1 | Pseudomonas | 假单胞菌属 | 364 | 257 | 1 | 1 | 134 | 95 | G- | 0.03 | 3.79 | 0.009 | 1.1009 | - | - | id¦54071267¦BAC¦R_0852907¦ | id¦08199131¦BAC¦S_7913979¦
source water 2 | Acinetobacter_junii | 琼氏不动杆菌 | 420/3334416 | 0.0126 | 1 | 15 | 9 | Acinetobacter | 不动杆菌属 | 261 | 219 | 6 | 3 | 96 | 81 | G- | 0.29 | 4.68 | 0.083 | 1.3598 | 1 | 0.96 | id¦83436215¦BAC¦R_6577620¦ | id¦62389735¦BAC¦S_6702589¦
source water 2 | Acinetobacter_lwoffii | 洛菲不动杆菌 | 478/3307394 | 0.0145 | 1.05 | 22 | 5 | Acinetobacter | 不动杆菌属 | 261 | 219 | 8 | 2 | 96 | 81 | G- | 0.42 | 4.68 | 0.1227 | 1.3598 | 0.95 | 0.94 | id¦99195648¦BAC¦R_5312259¦ | id¦42773179¦BAC¦S_0400613¦
source water 2 | Acinetobacter_radioresistens | 抗辐射不动杆菌 | 168/3393065 | 0.005 | 1 | 5 | 3 | Acinetobacter | 不动杆菌属 | 261 | 219 | 2 | 1 | 96 | 81 | G- | 0.09 | 4.68 | 0.0272 | 1.3598 | 1 | 0.63 | id¦43764125¦BAC¦R_9966152¦ | id¦33982299¦BAC¦S_0564958¦
source water 2 | Acinetobacter_soli | 土壤不动杆菌 | 168/3575309 | 0.0047 | 1 | 5 | 3 | Acinetobacter | 不动杆菌属 | 261 | 219 | 2 | 1 | 96 | 81 | G- | 0.09 | 4.68 | 0.0258 | 1.3598 | 1 | 0.51 | id¦82255082¦BAC¦R_0672257¦ | id¦07686929¦BAC¦S_8032167¦
source water 2 | Acinetobacter_piscicola | 栖鱼不动杆菌 | 84/3814463 | 0.0022 | 1 | 2 | 2 | Acinetobacter | 不动杆菌属 | 261 | 219 | 1 | 1 | 96 | 81 | G- | 0.03 | 4.68 | 0.0097 | 1.3598 | - | - | id¦48188939¦BAC¦R_4302827¦ | id¦14571039¦BAC¦S_4088475¦
source water 2 | Corynebacterium_striatum | 纹带棒杆菌 | 252/2790902 | 0.009 | 1 | 7 | 6 | Corynebacterium | 棒杆菌属 | 166 | 121 | 3 | 2 | 61 | 45 | G+ | 0.16 | 4.16 | 0.0463 | 1.2083 | 1 | 0.92 | id¦68846109¦BAC¦R_4445394¦ | id¦42438174¦BAC¦S_8998241¦
source water 2 | Corynebacterium_glucuronolyticum | 解谷氨酸棒杆菌 | 286/2823579 | 0.0101 | 1.03 | 7 | 5 | Corynebacterium | 棒杆菌属 | 166 | 121 | 3 | 2 | 61 | 45 | G+ | 0.16 | 4.16 | 0.0457 | 1.2083 | 0.97 | 0.62 | id¦88964123¦BAC¦R_5203628¦ | id¦23262570¦BAC¦S_2089341¦
source water 2 | Corynebacterium_tuberculostearicum | 结核硬脂酸棒杆菌 | 1043/2453172 | 0.0425 | 1 | 32 | 5 | Corynebacterium | 棒杆菌属 | 166 | 121 | 12 | 2 | 61 | 45 | G+ | 0.83 | 4.16 | 0.2407 | 1.2083 | 1 | 0.93 | id¦19707555¦BAC¦R_2204996¦ | id¦16312142¦BAC¦S_0227174¦
source water 2 | Corynebacterium_kroppenstedtii | 克罗彭施泰特棒杆菌 | 168/2571443 | 0.0065 | 1 | 4 | 4 | Corynebacterium | 棒杆菌属 | 166 | 121 | 1 | 1 | 61 | 45 | G+ | 0.1 | 4.16 | 0.0287 | 1.2083 | 1 | 0.63 | id¦59694191¦BAC¦R_1704994¦ | id¦78634322¦BAC¦S_1017763¦
source water 2 | Corynebacterium_variabile | 变异棒杆菌 | 177/3433007 | 0.0052 | 1.19 | 6 | 3 | Corynebacterium | 棒杆菌属 | 166 | 121 | 2 | 1 | 61 | 45 | G+ | 0.11 | 4.16 | 0.0323 | 1.2083 | 0.84 | 0.46 | id¦78694207¦BAC¦R_7467374¦ | id¦15770399¦BAC¦S_9924435¦
source water 2 | Corynebacterium_aurimucosum | 金色黏液棒杆菌 | 924/2419664 | 0.0382 | 1 | 28 | 2 | Corynebacterium | 棒杆菌属 | 166 | 121 | 10 | 1 | 61 | 45 | G+ | 0.74 | 4.16 | 0.2135 | 1.2083 | 1 | 0.99 | id¦40822602¦BAC¦R_2654121¦ | id¦32606643¦BAC¦S_5621655¦
source water 2 | Corynebacterium_jeikeium | 杰氏棒杆菌 | 126/2462499 | 0.0051 | 1 | 6 | 2 | Corynebacterium | 棒杆菌属 | 166 | 121 | 2 | 1 | 61 | 45 | G+ | 0.15 | 4.16 | 0.045 | 1.2083 | - | - | id¦09415763¦BAC¦R_8806879¦ | id¦23161981¦BAC¦S_5366700¦
source water 2 | Corynebacterium_kefirresidentii | 棒杆菌* | 420/2508302 | 0.0167 | 1 | 10 | 2 | Corynebacterium | 棒杆菌属 | 166 | 121 | 4 | 1 | 61 | 45 | G+ | 0.25 | 4.16 | 0.0736 | 1.2083 | 1 | 0.96 | id¦95009171¦BAC¦R_3817316¦ | id¦54970579¦BAC¦S_3204552¦
source water 2 | Corynebacterium_testudinoris | 龟口腔棒杆菌 | 84/2721226 | 0.0031 | 1 | 2 | 2 | Corynebacterium | 棒杆菌属 | 166 | 121 | 1 | 1 | 61 | 45 | G+ | 0.05 | 4.16 | 0.0136 | 1.2083 | - | - | id¦06256605¦BAC¦R_7479174¦ | id¦32448068¦BAC¦S_0516734¦
source water 2 | Corynebacterium_casei | 乳酪棒杆菌 | 42/3113488 | 0.0013 | 1 | 1 | 1 | Corynebacterium | 棒杆菌属 | 166 | 121 | 1 | 1 | 61 | 45 | G+ | 0.02 | 4.16 | 0.0059 | 1.2083 | - | - | id¦94272411¦BAC¦R_9634410¦ | id¦51900213¦BAC¦S_7711282¦
source water 2 | Ralstonia_insidiosa | 危险罗尔斯顿菌 | 374/5808308 | 0.0064 | 1 | 14 | 8 | Ralstonia | 罗尔斯顿菌属 | 141 | 115 | 5 | 3 | 52 | 42 | G- | 0.15 | 1.63 | 0.0445 | 0.4727 | 1 | 0.97 | id¦84272409¦BAC¦R_0490810¦ | id¦44746198¦BAC¦S_8470464¦
source water 2 | Ralstonia_mannitolilytica | 解甘露醇罗尔斯顿菌 | 84/5084427 | 0.0017 | 1 | 3 | 1 | Ralstonia | 罗尔斯顿菌属 | 141 | 115 | 1 | 1 | 52 | 42 | G- | 0.04 | 1.63 | 0.0109 | 0.4727 | - | - | id¦37675829¦BAC¦R_4471266¦ | id¦01120019¦BAC¦S_3094637¦
source water 2 | Staphylococcus_nepalensis | 尼泊尔葡萄球菌 | 84/2941886 | 0.0029 | 1 | 2 | 2 | Staphylococcus | 葡萄球菌属 | 118 | 109 | 1 | 1 | 44 | 40 | G+ | 0.04 | 2.99 | 0.0125 | 0.8676 | - | - | id¦81479237¦BAC¦R_2081866¦ | id¦45277114¦BAC¦S_6049993¦
source water 2 | Staphylococcus_warneri | 沃氏葡萄球菌 | 168/2515743 | 0.0067 | 1 | 4 | 2 | Staphylococcus | 葡萄球菌属 | 118 | 109 | 1 | 1 | 44 | 40 | G+ | 0.1 | 2.99 | 0.0293 | 0.8676 | 1 | 0 | id¦75446647¦BAC¦R_3071357¦ | id¦45505922¦BAC¦S_5631770¦
source water 2 | Staphylococcus_caprae | 山羊葡萄球菌 | 42/2662916 | 0.0016 | 1 | 1 | 1 | Staphylococcus | 葡萄球菌属 | 118 | 109 | 1 | 1 | 44 | 40 | G+ | 0.02 | 2.99 | 0.0069 | 0.8676 | - | - | id¦14983607¦BAC¦R_0197917¦ | id¦73673807¦BAC¦S_4123533¦
source water 2 | Staphylococcus_cohnii | 科氏葡萄球菌 | 42/2665141 | 0.0016 | 1 | 1 | 1 | Staphylococcus | 葡萄球菌属 | 118 | 109 | 1 | 1 | 44 | 40 | G+ | 0.02 | 2.99 | 0.0069 | 0.8676 | - | - | id¦02391944¦BAC¦R_3719972¦ | id¦05632411¦BAC¦S_0400933¦
source water 2 | Staphylococcus_haemolyticus | 溶血葡萄球菌 | 84/2699292 | 0.0031 | 1 | 2 | 1 | Staphylococcus | 葡萄球菌属 | 118 | 109 | 1 | 1 | 44 | 40 | G+ | 0.05 | 2.99 | 0.0137 | 0.8676 | - | - | id¦33823453¦BAC¦R_4061613¦ | id¦21767703¦BAC¦S_6480655¦
source water 2 | Staphylococcus_lugdunensis | 路邓葡萄球菌 | 42/2694981 | 0.0016 | 1 | 1 | 1 | Staphylococcus | 葡萄球菌属 | 118 | 109 | 1 | 1 | 44 | 40 | G+ | 0.02 | 2.99 | 0.0068 | 0.8676 | - | - | id¦51368684¦BAC¦R_4403851¦ | id¦18899560¦BAC¦S_8577929¦
source water 2 | Staphylococcus_pettenkoferi | 佩滕科夫葡萄球菌 | 42/2498046 | 0.0017 | 1 | 1 | 1 | Staphylococcus | 葡萄球菌属 | 118 | 109 | 1 | 1 | 44 | 40 | G+ | 0.03 | 2.99 | 0.0074 | 0.8676 | - | - | id¦34013675¦BAC¦R_4157690¦ | id¦43498178¦BAC¦S_8828073¦
source water 2 | Caldicellulosiruptor_acetigenus | 产乙酸热解纤维素菌 | 771/2590317 | 0.0298 | 1 | 19 | 3 | Caldicellulosiruptor | 热解纤维素菌属 | 111 | 86 | 7 | 1 | 41 | 32 | G+ | 0.47 | 2.62 | 0.1354 | 0.7619 | 1 | 0.98 | id¦57266958¦BAC¦R_7258166¦ | id¦69708929¦BAC¦S_5914124¦
source water 2 | Caldicellulosiruptor_hydrothermalis | 热液口热解纤维素菌 | 395/2770676 | 0.0143 | 1.04 | 10 | 3 | Caldicellulosiruptor | 热解纤维素菌属 | 111 | 86 | 4 | 1 | 41 | 32 | G+ | 0.23 | 2.62 | 0.0666 | 0.7619 | 0.96 | 0.56 | id¦54464017¦BAC¦R_5017448¦ | id¦38853811¦BAC¦S_4187457¦
source water 2 | Caldicellulosiruptor_lactoaceticus | 产乳酸乙酸热解纤维素菌 | 1035/2674809 | 0.0387 | 1 | 25 | 2 | Caldicellulosiruptor | 热解纤维素菌属 | 111 | 86 | 9 | 1 | 41 | 32 | G+ | 0.59 | 2.62 | 0.1725 | 0.7619 | 1 | 0.99 | id¦59644528¦BAC¦R_1889121¦ | id¦16662092¦BAC¦S_2346312¦
source water 2 | Caldicellulosiruptor_kristjanssonii | 克氏热解纤维素菌 | 778/2786473 | 0.0279 | 1 | 19 | 1 | Caldicellulosiruptor | 热解纤维素菌属 | 111 | 86 | 7 | 1 | 41 | 32 | G+ | 0.43 | 2.62 | 0.1258 | 0.7619 | 1 | 0.96 | id¦26555964¦BAC¦R_2672383¦ | id¦16729194¦BAC¦S_1030333¦
source water 2 | Caldicellulosiruptor_kronotskyensis | 克罗诺基热解纤维素菌 | 252/2843785 | 0.0089 | 1 | 6 | 1 | Caldicellulosiruptor | 热解纤维素菌属 | 111 | 86 | 2 | 1 | 41 | 32 | G+ | 0.13 | 2.62 | 0.0389 | 0.7619 | 1 | 0.58 | id¦17446996¦BAC¦R_2911553¦ | id¦03658968¦BAC¦S_4218070¦
source water 2 | Caldicellulosiruptor_owensensis | 欧文氏热解纤维素菌 | 165/2428903 | 0.0068 | 1.02 | 7 | 1 | Caldicellulosiruptor | 热解纤维素菌属 | 111 | 86 | 3 | 1 | 41 | 32 | G+ | 0.18 | 2.62 | 0.0532 | 0.7619 | 0.98 | 0.51 | id¦63083332¦BAC¦R_9062676¦ | id¦19959773¦BAC¦S_9069934¦
source water 2 | Caldicellulosiruptor_saccharolyticus | 解糖热解纤维素菌 | 161/2970275 | 0.0054 | 1 | 4 | 1 | Caldicellulosiruptor | 热解纤维素菌属 | 111 | 86 | 1 | 1 | 41 | 32 | G+ | 0.09 | 2.62 | 0.0249 | 0.7619 | 1 | 0.51 | id¦76187509¦BAC¦R_1534187¦ | id¦97453204¦BAC¦S_9474322¦
source water 2 | Altererythrobacter_buctensis | 北京化工大交替赤杆菌 | 42/3773064 | 0.0011 | 1 | 1 | 1 | Altererythrobacter | 交替赤杆菌属 | 92 | 66 | 1 | 1 | 34 | 24 | G- | 0.02 | 2.01 | 0.0049 | 0.584 | - | - | id¦47895213¦BAC¦R_8534225¦ | id¦38405418¦BAC¦S_5835538¦
source water 2 | Pseudoxanthomonas_japonensis | 日本假黄单胞菌 | 672/4065943 | 0.0165 | 1 | 16 | 7 | Pseudoxanthomonas | 假黄单胞菌属 | 126 | 64 | 6 | 3 | 47 | 24 | G- | 0.25 | 2.07 | 0.0726 | 0.6007 | 1 | 1 | id¦38446314¦BAC¦R_0506597¦ | id¦64490526¦BAC¦S_9280671¦
source water 2 | Pseudoxanthomonas_kaohsiungensis | 高雄假黄单胞菌 | 255/3735093 | 0.0068 | 1.15 | 7 | 3 | Pseudoxanthomonas | 假黄单胞菌属 | 126 | 64 | 3 | 1 | 47 | 24 | G- | 0.12 | 2.07 | 0.0346 | 0.6007 | 0.87 | 0.91 | id¦06353043¦BAC¦R_5416493¦ | id¦47893531¦BAC¦S_3963593¦
source water 2 | Pseudoxanthomonas_indica | 印度假黄单胞菌 | 122/3960936 | 0.0031 | 1 | 3 | 1 | Pseudoxanthomonas | 假黄单胞菌属 | 126 | 64 | 1 | 1 | 47 | 24 | G- | 0.05 | 2.07 | 0.014 | 0.6007 | - | - | id¦52806577¦BAC¦R_4163123¦ | id¦29081366¦BAC¦S_6914620¦
source water 2 | Pseudoxanthomonas_spadix | 褐色假黄单胞菌 | 80/4669877 | 0.0017 | 1 | 3 | 1 | Pseudoxanthomonas | 假黄单胞菌属 | 126 | 64 | 1 | 1 | 47 | 24 | G- | 0.04 | 2.07 | 0.0119 | 0.6007 | - | - | id¦53894863¦BAC¦R_2943111¦ | id¦89243648¦BAC¦S_0997163¦
source water 2 | Cedecea_lapagei | 拉帕西地西菌 | 84/4778444 | 0.0018 | 1 | 2 | 1 | Cedecea | 西地西菌属 | 109 | 60 | 1 | 1 | 40 | 22 | G- | 0.03 | 1.4 | 0.0077 | 0.4056 | - | - | id¦76373265¦BAC¦R_2182340¦ | id¦82324835¦BAC¦S_1383020¦
source water 2 | Moraxella_atlantae | 亚特兰大莫拉菌 | 115/2501709 | 0.0046 | 1 | 3 | 1 | Moraxella | 莫拉菌属 | 74 | 60 | 1 | 1 | 27 | 22 | G- | 0.08 | 1.93 | 0.0221 | 0.5591 | - | - | id¦49691506¦BAC¦R_8398575¦ | id¦80015982¦BAC¦S_1758229¦
source water 2 | Streptococcus_parasanguinis | 副血链球菌 | 168/2270733 | 0.0074 | 1 | 7 | 6 | Streptococcus | 链球菌属 | 67 | 58 | 3 | 2 | 25 | 21 | G+ | 0.2 | 2.05 | 0.0569 | 0.5964 | 1 | 0.95 | id¦22398429¦BAC¦R_5557567¦ | id¦39376444¦BAC¦S_8063262¦
source water 2 | Streptococcus_oralis | 口腔链球菌 | 164/1872903 | 0.0088 | 1 | 7 | 3 | Streptococcus | 链球菌属 | 67 | 58 | 3 | 1 | 25 | 21 | G+ | 0.24 | 2.05 | 0.069 | 0.5964 | 1 | 0.51 | id¦66920924¦BAC¦R_4690967¦ | id¦41327418¦BAC¦S_7770086¦
source water 2 | Streptococcus_sanguinis | 血链球菌 | 126/2388435 | 0.0053 | 1 | 6 | 3 | Streptococcus | 链球菌属 | 67 | 58 | 2 | 1 | 25 | 21 | G+ | 0.16 | 2.05 | 0.0464 | 0.5964 | - | - | id¦30808801¦BAC¦R_9531876¦ | id¦24531979¦BAC¦S_9217069¦
source water 2 | Streptococcus_infantis | 婴儿链球菌 | 84/1792091 | 0.0047 | 1 | 6 | 2 | Streptococcus | 链球菌属 | 67 | 58 | 2 | 1 | 25 | 21 | G+ | 0.21 | 2.05 | 0.0618 | 0.5964 | - | - | id¦12124404¦BAC¦R_4845525¦ | id¦38632365¦BAC¦S_7649912¦
source water 2 | Streptococcus_australis | 南方链球菌 | 84/1928637 | 0.0044 | 1 | 3 | 1 | Streptococcus | 链球菌属 | 67 | 58 | 1 | 1 | 25 | 21 | G+ | 0.1 | 2.05 | 0.0287 | 0.5964 | - | - | id¦38182515¦BAC¦R_1944817¦ | id¦55753248¦BAC¦S_3346604¦
source water 2 | Streptococcus_infantarius | 小儿链球菌 | 42/1988420 | 0.0021 | 1 | 1 | 1 | Streptococcus | 链球菌属 | 67 | 58 | 1 | 1 | 25 | 21 | G+ | 0.03 | 2.05 | 0.0093 | 0.5964 | - | - | id¦02561294¦BAC¦R_0475754¦ | id¦43387261¦BAC¦S_0069303¦
source water 2 | Streptococcus_mitis | 缓症链球菌 | 126/2099603 | 0.006 | 1 | 9 | 1 | Streptococcus | 链球菌属 | 67 | 58 | 3 | 1 | 25 | 21 | G+ | 0.27 | 2.05 | 0.0791 | 0.5964 | - | - | id¦88049982¦BAC¦R_5806823¦ | id¦71856117¦BAC¦S_5870034¦
source water 2 | Streptococcus_salivarius | 唾液链球菌 | 126/2322111 | 0.0054 | 1 | 4 | 1 | Streptococcus | 链球菌属 | 67 | 58 | 1 | 1 | 25 | 21 | G+ | 0.11 | 2.05 | 0.0318 | 0.5964 | - | - | id¦34519581¦BAC¦R_8132101¦ | id¦87078916¦BAC¦S_8037111¦
source water 2 | Streptococcus_sp._I-P16 | 链球菌I-P16 | 42/2023580 | 0.0021 | 1 | 1 | 1 | Streptococcus | 链球菌属 | 67 | 58 | 1 | 1 | 25 | 21 | G+ | 0.03 | 2.05 | 0.0091 | 0.5964 | - | - | id¦76345525¦BAC¦R_1280322¦ | id¦45050604¦BAC¦S_1511555¦
source water 2 | Streptococcus_thermophilus | 嗜热链球菌 | 42/2053706 | 0.002 | 1 | 1 | 1 | Streptococcus | 链球菌属 | 67 | 58 | 1 | 1 | 25 | 21 | G+ | 0.03 | 2.05 | 0.009 | 0.5964 | - | - | id¦65350792¦BAC¦R_6412800¦ | id¦29716721¦BAC¦S_6565212¦
source water 2 | Micrococcus_endophyticus | 植物内生微球菌 | 168/1100928 | 0.0153 | 1 | 4 | 4 | Micrococcus | 微球菌属 | 64 | 54 | 1 | 1 | 24 | 20 | G+ | 0.23 | 1.74 | 0.067 | 0.5064 | 1 | 0.51 | id¦32544843¦BAC¦R_0182842¦ | id¦88860031¦BAC¦S_9344633¦
source water 2 | Micrococcus_luteus | 藤黄微球菌 | 1004/2518819 | 0.0399 | 1 | 39 | 4 | Micrococcus | 微球菌属 | 64 | 54 | 14 | 1 | 24 | 20 | G+ | 0.98 | 1.74 | 0.2857 | 0.5064 | 1 | 0.99 | id¦54995006¦BAC¦R_7796282¦ | id¦80537523¦BAC¦S_1440446¦
source water 2 | Micrococcus_yunnanensis | 云南微球菌 | 210/2463995 | 0.0085 | 1 | 6 | 2 | Micrococcus | 微球菌属 | 64 | 54 | 2 | 1 | 24 | 20 | G+ | 0.15 | 1.74 | 0.0449 | 0.5064 | 1 | 0.61 | id¦02646806¦BAC¦R_9224781¦ | id¦07465033¦BAC¦S_0037293¦
source water 2 | Micrococcus_terreus | 土微球菌 | 42/3087820 | 0.0014 | 1 | 1 | 1 | Micrococcus | 微球菌属 | 64 | 54 | 1 | 1 | 24 | 20 | G+ | 0.02 | 1.74 | 0.006 | 0.5064 | - | - | id¦58203890¦BAC¦R_2437942¦ | id¦66191775¦BAC¦S_0069957¦
source water 2 | Brevundimonas_diminuta | 缺陷短波单胞菌 | 788/3551819 | 0.0222 | 1 | 28 | 7 | Brevundimonas | 短波单胞菌属 | 69 | 45 | 10 | 3 | 25 | 17 | G- | 0.5 | 1.3 | 0.1455 | 0.3778 | 1 | 0.95 | id¦29759199¦BAC¦R_6904079¦ | id¦88190477¦BAC¦S_0780681¦
source water 2 | Brevundimonas_vesicularis | 泡囊短波单胞菌 | 336/3345527 | 0.01 | 1 | 15 | 7 | Brevundimonas | 短波单胞菌属 | 69 | 45 | 6 | 3 | 25 | 17 | G- | 0.28 | 1.3 | 0.0827 | 0.3778 | 1 | 0.82 | id¦46097836¦BAC¦R_5267318¦ | id¦56496784¦BAC¦S_2888286¦
source water 2 | Brevundimonas_naejangsanensis | 内藏山短波单胞菌 | 126/2831868 | 0.0044 | 1 | 4 | 1 | Brevundimonas | 短波单胞菌属 | 69 | 45 | 1 | 1 | 25 | 17 | G- | 0.09 | 1.3 | 0.0261 | 0.3778 | - | - | id¦92026895¦BAC¦R_6914696¦ | id¦38522771¦BAC¦S_6566075¦
source water 2 | Brevundimonas_nasdae | 那斯达短波单胞菌 | 84/3400737 | 0.0025 | 1 | 2 | 1 | Brevundimonas | 短波单胞菌属 | 69 | 45 | 1 | 1 | 25 | 17 | G- | 0.04 | 1.3 | 0.0109 | 0.3778 | - | - | id¦13720706¦BAC¦R_7216837¦ | id¦59992167¦BAC¦S_3598523¦
source water 2 | Brevundimonas_subvibrioides | 近弧状短波单胞菌 | 126/3445263 | 0.0037 | 1 | 4 | 1 | Brevundimonas | 短波单胞菌属 | 69 | 45 | 1 | 1 | 25 | 17 | G- | 0.07 | 1.3 | 0.0214 | 0.3778 | - | - | id¦20333228¦BAC¦R_1613914¦ | id¦56227140¦BAC¦S_9664236¦
source water 2 | Acidovorax_delafieldii | 德氏食酸菌 | 252/4005465 | 0.0063 | 1 | 14 | 4 | Acidovorax | 食酸菌属 | 84 | 43 | 5 | 1 | 31 | 16 | G- | 0.22 | 1.17 | 0.0645 | 0.34 | 1 | 0.58 | id¦98828408¦BAC¦R_1005926¦ | id¦87965818¦BAC¦S_5899216¦
source water 2 | Acidovorax_carolinensis | 北卡罗来纳食酸菌 | 336/4077847 | 0.0082 | 1 | 11 | 2 | Acidovorax | 食酸菌属 | 84 | 43 | 4 | 1 | 31 | 16 | G- | 0.17 | 1.17 | 0.0498 | 0.34 | 1 | 0.82 | id¦99809340¦BAC¦R_9685281¦ | id¦23151307¦BAC¦S_0024136¦
source water 2 | Acidovorax_sp._KKS102 | 食酸菌KKS102 | 315/5196935 | 0.0061 | 1.07 | 8 | 1 | Acidovorax | 食酸菌属 | 84 | 43 | 3 | 1 | 31 | 16 | G- | 0.1 | 1.17 | 0.0284 | 0.34 | 0.94 | 0.95 | id¦72972274¦BAC¦R_2632165¦ | id¦11290306¦BAC¦S_8546691¦
source water 2 | Acidovorax_wautersii | 沃氏食酸菌 | 158/5331330 | 0.003 | 1 | 4 | 1 | Acidovorax | 食酸菌属 | 84 | 43 | 1 | 1 | 31 | 16 | G- | 0.05 | 1.17 | 0.0138 | 0.34 | 1 | 0.95 | id¦48237168¦BAC¦R_4276605¦ | id¦99192046¦BAC¦S_7173969¦
source water 2 | Thermus_scotoductus | 水管致黑栖热菌 | 660/2363025 | 0.0279 | 1.01 | 24 | 9 | Thermus | 栖热菌属 | 45 | 40 | 9 | 3 | 17 | 15 | G- | 0.65 | 1.31 | 0.1874 | 0.3811 | 0.99 | 0.95 | id¦73472961¦BAC¦R_7815903¦ | id¦62537656¦BAC¦S_4433354¦
source water 2 | Thermus_thermophilus | 嗜热栖热菌 | 412/1902595 | 0.0217 | 1 | 12 | 3 | Thermus | 栖热菌属 | 45 | 40 | 4 | 1 | 17 | 15 | G- | 0.4 | 1.31 | 0.1164 | 0.3811 | 1 | 0.82 | id¦16880787¦BAC¦R_1780603¦ | id¦20203455¦BAC¦S_4838763¦
source water 2 | Sphingomonas_echinoides | 多刺形鞘氨醇单胞菌 | 588/4180637 | 0.0141 | 1 | 14 | 7 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 5 | 3 | 35 | 14 | G- | 0.21 | 1.56 | 0.0618 | 0.452 | 1 | 0.87 | id¦49048856¦BAC¦R_8015597¦ | id¦25279112¦BAC¦S_2088235¦
source water 2 | Sphingomonas_kaistensis | 凯斯特鞘氨醇单胞菌 | 627/2846238 | 0.022 | 1.06 | 16 | 5 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 6 | 2 | 35 | 14 | G- | 0.36 | 1.56 | 0.1037 | 0.452 | 0.95 | 0.62 | id¦11255785¦BAC¦R_7946770¦ | id¦01222679¦BAC¦S_0715446¦
source water 2 | Sphingomonas_paucimobilis | 少动鞘氨醇单胞菌 | 290/4572304 | 0.0063 | 1 | 9 | 4 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 3 | 1 | 35 | 14 | G- | 0.13 | 1.56 | 0.0363 | 0.452 | 1 | 0.91 | id¦58760997¦BAC¦R_1060066¦ | id¦49350332¦BAC¦S_4242188¦
source water 2 | Sphingomonas_sanguinis | 血红鞘氨醇单胞菌 | 168/4480941 | 0.0037 | 1 | 9 | 3 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 3 | 1 | 35 | 14 | G- | 0.13 | 1.56 | 0.0371 | 0.452 | 1 | 0.95 | id¦84126773¦BAC¦R_5913676¦ | id¦98159255¦BAC¦S_7712449¦
source water 2 | Sphingomonas_histidinilytica | 解组氨酸鞘氨醇单胞菌 | 80/5473919 | 0.0015 | 1 | 2 | 2 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 1 | 1 | 35 | 14 | G- | 0.02 | 1.56 | 0.0067 | 0.452 | - | - | id¦83701616¦BAC¦R_0796824¦ | id¦21928564¦BAC¦S_2806224¦
source water 2 | Sphingomonas_adhaesiva | 粘连鞘氨醇单胞菌 | 84/3987712 | 0.0021 | 1 | 2 | 1 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 1 | 1 | 35 | 14 | G- | 0.03 | 1.56 | 0.0093 | 0.452 | - | - | id¦71282086¦BAC¦R_4800270¦ | id¦11685654¦BAC¦S_9232804¦
source water 2 | Sphingomonas_asaccharolytica | 不解糖鞘氨醇单胞菌 | 40/4601844 | 0.0009 | 1 | 1 | 1 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 1 | 1 | 35 | 14 | G- | 0.01 | 1.56 | 0.004 | 0.452 | - | - | id¦03081327¦BAC¦R_6812832¦ | id¦73232175¦BAC¦S_1637914¦
source water 2 | Sphingomonas_desiccabilis | 可干鞘氨醇单胞菌 | 84/3607051 | 0.0023 | 1 | 2 | 1 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 1 | 1 | 35 | 14 | G- | 0.04 | 1.56 | 0.0102 | 0.452 | - | - | id¦45690181¦BAC¦R_7700657¦ | id¦94954993¦BAC¦S_5642660¦
source water 2 | Sphingomonas_glacialis | 冰川鞘氨醇单胞菌 | 63/5120783 | 0.0012 | 1.33 | 2 | 1 | Sphingomonas | 鞘氨醇单胞菌属 | 95 | 38 | 1 | 1 | 35 | 14 | G- | 0.02 | 1.56 | 0.0072 | 0.452 | - | - | id¦03867785¦BAC¦R_9430722¦ | id¦87001650¦BAC¦S_2485431¦
source water 2 | Burkholderia_cepacia | 洋葱伯克霍尔德菌 | 420/9514203 | 0.0044 | 1 | 16 | 3 | Burkholderia | 伯克霍尔德菌属 | 49 | 35 | 6 | 1 | 18 | 13 | G- | 0.11 | 0.36 | 0.031 | 0.1041 | 1 | 0.86 | id¦51831238¦BAC¦R_2477297¦ | id¦79817129¦BAC¦S_9425609¦
source water 2 | Burkholderia_contaminans | 污染伯克霍尔德菌 | 252/8761548 | 0.0029 | 1 | 6 | 2 | Burkholderia | 伯克霍尔德菌属 | 49 | 35 | 2 | 1 | 18 | 13 | G- | 0.04 | 0.36 | 0.0126 | 0.1041 | 1 | 0.92 | id¦08103812¦BAC¦R_8005672¦ | id¦69725635¦BAC¦S_9905471¦
source water 2 | Burkholderia_cenocepacia | 新洋葱伯克霍尔德菌 | 168/8531679 | 0.002 | 1 | 6 | 1 | Burkholderia | 伯克霍尔德菌属 | 49 | 35 | 2 | 1 | 18 | 13 | G- | 0.04 | 0.36 | 0.013 | 0.1041 | 1 | 0.63 | id¦04944442¦BAC¦R_3796017¦ | id¦47633230¦BAC¦S_7638737¦
source water 2 | Paracoccus_sphaerophysae | 苦马豆副球菌 | 336/3355089 | 0.01 | 1 | 8 | 8 | Paracoccus | 副球菌属 | 80 | 35 | 3 | 3 | 30 | 13 | G- | 0.15 | 1.37 | 0.044 | 0.3974 | 1 | 0.95 | id¦75714865¦BAC¦R_7943103¦ | id¦90637328¦BAC¦S_9453463¦
source water 2 | Paracoccus_marinus | 滨海副球菌 | 168/3123755 | 0.0054 | 1 | 4 | 4 | Paracoccus | 副球菌属 | 80 | 35 | 1 | 1 | 30 | 13 | G- | 0.08 | 1.37 | 0.0236 | 0.3974 | 1 | 0 | id¦56010813¦BAC¦R_9036646¦ | id¦64668586¦BAC¦S_1905079¦
source water 2 | Paracoccus_sanguinis | 血副球菌 | 84/3409589 | 0.0025 | 1 | 4 | 4 | Paracoccus | 副球菌属 | 80 | 35 | 1 | 1 | 30 | 13 | G- | 0.07 | 1.37 | 0.0216 | 0.3974 | - | - | id¦94597985¦BAC¦R_0848814¦ | id¦19071542¦BAC¦S_2665970¦
source water 2 | Paracoccus_chinensis | 中华副球菌 | 113/3633700 | 0.0031 | 1.12 | 3 | 2 | Paracoccus | 副球菌属 | 80 | 35 | 1 | 1 | 30 | 13 | G- | 0.05 | 1.37 | 0.0152 | 0.3974 | - | - | id¦69158942¦BAC¦R_6058228¦ | id¦41562470¦BAC¦S_5448745¦
source water 2 | Paracoccus_marcusii | 马氏副球菌 | 126/3653673 | 0.0034 | 1 | 3 | 2 | Paracoccus | 副球菌属 | 80 | 35 | 1 | 1 | 30 | 13 | G- | 0.05 | 1.37 | 0.0152 | 0.3974 | - | - | id¦55983350¦BAC¦R_3491635¦ | id¦10340487¦BAC¦S_2846803¦
source water 2 | Paracoccus_sediminis | 沉积物副球菌 | 374/3646141 | 0.0103 | 1 | 9 | 2 | Paracoccus | 副球菌属 | 80 | 35 | 3 | 1 | 30 | 13 | G- | 0.16 | 1.37 | 0.0455 | 0.3974 | 1 | 0.91 | id¦79034600¦BAC¦R_0608582¦ | id¦41244491¦BAC¦S_1739464¦
source water 2 | Paracoccus_hibiscisoli | 木槿土副球菌 | 84/3951219 | 0.0021 | 1 | 2 | 1 | Paracoccus | 副球菌属 | 80 | 35 | 1 | 1 | 30 | 13 | G- | 0.03 | 1.37 | 0.0093 | 0.3974 | - | - | id¦70336303¦BAC¦R_4108043¦ | id¦84877359¦BAC¦S_6302789¦
source water 2 | Paracoccus_salipaludis | 盐沼副球菌 | 84/3612022 | 0.0023 | 1 | 2 | 1 | Paracoccus | 副球菌属 | 80 | 35 | 1 | 1 | 30 | 13 | G- | 0.04 | 1.37 | 0.0102 | 0.3974 | - | - | id¦93777267¦BAC¦R_0130146¦ | id¦76184229¦BAC¦S_7881470¦
source water 2 | Caulobacter_henricii | 亨氏柄杆菌 | 77/3864204 | 0.002 | 1 | 4 | 1 | Caulobacter | 柄杆菌属 | 69 | 33 | 1 | 1 | 25 | 12 | G- | 0.07 | 1 | 0.0191 | 0.2914 | - | - | id¦44101039¦BAC¦R_4899738¦ | id¦34177290¦BAC¦S_0243795¦
source water 2 | Caulobacter_segnis | 惰性柄杆菌 | 378/4655622 | 0.0081 | 1 | 11 | 1 | Caulobacter | 柄杆菌属 | 69 | 33 | 4 | 1 | 25 | 12 | G- | 0.15 | 1 | 0.0436 | 0.2914 | 1 | 0.48 | id¦06754409¦BAC¦R_1614008¦ | id¦42807857¦BAC¦S_2392370¦
source water 2 | Rhodococcus_fascians | 束红球菌 | 168/6080144 | 0.0028 | 1 | 8 | 5 | Rhodococcus | 红球菌属 | 39 | 33 | 3 | 2 | 14 | 12 | G+ | 0.08 | 0.4 | 0.0243 | 0.1171 | 1 | 0.95 | id¦29743501¦BAC¦R_8216645¦ | id¦12406773¦BAC¦S_0484691¦
source water 2 | Rhodococcus_aetherivorans | 食醚红球菌 | 42/6628481 | 0.0006 | 1 | 1 | 1 | Rhodococcus | 红球菌属 | 39 | 33 | 1 | 1 | 14 | 12 | G+ | 0.01 | 0.4 | 0.0028 | 0.1171 | - | - | id¦42190830¦BAC¦R_4004598¦ | id¦21862714¦BAC¦S_3310575¦
source water 2 | Rhodococcus_enclensis | 印度国化室红球菌?? | 168/7209441 | 0.0023 | 1 | 4 | 1 | Rhodococcus | 红球菌属 | 39 | 33 | 1 | 1 | 14 | 12 | G+ | 0.04 | 0.4 | 0.0102 | 0.1171 | 1 | 0.95 | id¦44872495¦BAC¦R_7532662¦ | id¦98901954¦BAC¦S_7747985¦
source water 2 | Rhodococcus_erythropolis | 红串红球菌 | 168/6774290 | 0.0025 | 1 | 7 | 1 | Rhodococcus | 红球菌属 | 39 | 33 | 3 | 1 | 14 | 12 | G+ | 0.07 | 0.4 | 0.0191 | 0.1171 | 1 | 0.95 | id¦35953192¦BAC¦R_3413423¦ | id¦13861150¦BAC¦S_7169162¦
source water 2 | Rhodococcus_kroppenstedtii | 克罗彭施特红球菌 | 42/4025998 | 0.001 | 1 | 1 | 1 | Rhodococcus | 红球菌属 | 39 | 33 | 1 | 1 | 14 | 12 | G+ | 0.02 | 0.4 | 0.0046 | 0.1171 | - | - | id¦82587789¦BAC¦R_7383298¦ | id¦89095464¦BAC¦S_0199344¦
source water 2 | Rhodococcus_pyridinivorans | 嗜吡啶红球菌 | 168/5303895 | 0.0032 | 1 | 5 | 1 | Rhodococcus | 红球菌属 | 39 | 33 | 2 | 1 | 14 | 12 | G+ | 0.06 | 0.4 | 0.0174 | 0.1171 | 1 | 0.63 | id¦81729380¦BAC¦R_9725328¦ | id¦32624616¦BAC¦S_5179167¦
source water 2 | Rhodococcus_ruber | 赤红球菌 | 84/5669852 | 0.0015 | 1 | 2 | 1 | Rhodococcus | 红球菌属 | 39 | 33 | 1 | 1 | 14 | 12 | G+ | 0.02 | 0.4 | 0.0065 | 0.1171 | - | - | id¦34639082¦BAC¦R_9640785¦ | id¦87249633¦BAC¦S_4949563¦
source water 2 | Rhodococcus_zopfii | 佐氏红球菌 | 42/6284169 | 0.0007 | 1 | 1 | 1 | Rhodococcus | 红球菌属 | 39 | 33 | 1 | 1 | 14 | 12 | G+ | 0.01 | 0.4 | 0.0029 | 0.1171 | - | - | id¦23654863¦BAC¦R_2133113¦ | id¦40850239¦BAC¦S_6705077¦
source water 2 | Bacillus_coagulans | 凝结芽胞杆菌 | 42/3073079 | 0.0014 | 1 | 2 | 2 | Bacillus | 芽胞杆菌属 | 35 | 31 | 1 | 1 | 13 | 11 | G+ | 0.04 | 0.48 | 0.012 | 0.1407 | - | - | id¦07823554¦BAC¦R_2543729¦ | id¦73577487¦BAC¦S_0270116¦
source water 2 | Bacillus_licheniformis | 地衣芽胞杆菌 | 752/4747546 | 0.0158 | 1 | 21 | 2 | Bacillus | 芽胞杆菌属 | 35 | 31 | 8 | 1 | 13 | 11 | G+ | 0.28 | 0.48 | 0.0816 | 0.1407 | 1 | 0.99 | id¦07762770¦BAC¦R_9053297¦ | id¦11773467¦BAC¦S_7708432¦
source water 2 | Bacillus_circulans | 环状芽胞杆菌 | 42/5179558 | 0.0008 | 1 | 1 | 1 | Bacillus | 芽胞杆菌属 | 35 | 31 | 1 | 1 | 13 | 11 | G+ | 0.01 | 0.48 | 0.0036 | 0.1407 | - | - | id¦11451234¦BAC¦R_4630625¦ | id¦07354345¦BAC¦S_6438181¦
source water 2 | Bacillus_methanolicus | 甲醇芽胞杆菌 | 84/3405293 | 0.0025 | 1 | 2 | 1 | Bacillus | 芽胞杆菌属 | 35 | 31 | 1 | 1 | 13 | 11 | G+ | 0.04 | 0.48 | 0.0108 | 0.1407 | - | - | id¦36620827¦BAC¦R_1516610¦ | id¦53590774¦BAC¦S_1797219¦
source water 2 | Bacillus_thermoamylovorans | 热噬淀粉芽胞杆菌 | 42/4016170 | 0.001 | 1 | 1 | 1 | Bacillus | 芽胞杆菌属 | 35 | 31 | 1 | 1 | 13 | 11 | G+ | 0.02 | 0.48 | 0.0046 | 0.1407 | - | - | id¦74271046¦BAC¦R_0019897¦ | id¦28389882¦BAC¦S_7361258¦
source water 2 | Lactococcus_petauri | 蜜袋鼯乳球菌 | 42/2197976 | 0.0019 | 1 | 1 | 1 | Lactococcus | 乳球菌属 | 28 | 25 | 1 | 1 | 10 | 9 | G+ | 0.03 | 0.72 | 0.0084 | 0.2084 | - | - | id¦03046309¦BAC¦R_5785368¦ | id¦14681718¦BAC¦S_0110375¦
source water 2 | Brachybacterium_muris | 鼠小短杆菌 | 54/3253214 | 0.0017 | 1.56 | 2 | 2 | Brachybacterium | 小短杆菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G+ | 0.04 | 0.52 | 0.0113 | 0.1523 | - | - | id¦24249487¦BAC¦R_2977723¦ | id¦22711570¦BAC¦S_0111986¦
source water 2 | Brachybacterium_paraconglomeratum | 副凝聚小短杆菌 | 294/3784122 | 0.0078 | 1 | 8 | 2 | Brachybacterium | 小短杆菌属 | 32 | 23 | 3 | 1 | 12 | 8 | G+ | 0.13 | 0.52 | 0.039 | 0.1523 | 1 | 0.87 | id¦93848825¦BAC¦R_3355705¦ | id¦49034683¦BAC¦S_4138545¦
source water 2 | Brachybacterium_squillarum | 虾小短杆菌 | 77/3191549 | 0.0024 | 1.09 | 2 | 2 | Brachybacterium | 小短杆菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G+ | 0.04 | 0.52 | 0.0116 | 0.1523 | - | - | id¦16595085¦BAC¦R_2359508¦ | id¦01860499¦BAC¦S_5116230¦
source water 2 | Brachybacterium_massiliense | 小短杆菌* | 42/3865558 | 0.0011 | 1 | 1 | 1 | Brachybacterium | 小短杆菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.02 | 0.52 | 0.0048 | 0.1523 | - | - | id¦95929606¦BAC¦R_2712751¦ | id¦23569332¦BAC¦S_4410374¦
source water 2 | Brachybacterium_nesterenkovii | 涅氏小短杆菌 | 42/3023152 | 0.0014 | 1 | 1 | 1 | Brachybacterium | 小短杆菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G+ | 0.02 | 0.52 | 0.0061 | 0.1523 | - | - | id¦27726259¦BAC¦R_7469749¦ | id¦76805250¦BAC¦S_8819234¦
source water 2 | Prevotella_melaninogenica | 产黑色普雷沃菌 | 210/3168292 | 0.0066 | 1 | 8 | 4 | Prevotella | 普雷沃菌属 | 32 | 23 | 3 | 1 | 12 | 8 | G- | 0.16 | 0.66 | 0.0466 | 0.1906 | 1 | 0.96 | id¦88178094¦BAC¦R_9080140¦ | id¦61369871¦BAC¦S_1570876¦
source water 2 | Prevotella_aurantiaca | 桔红色普雷沃菌 | 84/2988619 | 0.0028 | 1 | 2 | 2 | Prevotella | 普雷沃菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.04 | 0.66 | 0.0123 | 0.1906 | - | - | id¦76320951¦BAC¦R_0593240¦ | id¦35692624¦BAC¦S_8489426¦
source water 2 | Prevotella_denticola | 栖牙普雷沃菌 | 42/2937589 | 0.0014 | 1 | 2 | 2 | Prevotella | 普雷沃菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.04 | 0.66 | 0.0126 | 0.1906 | - | - | id¦38948460¦BAC¦R_0025686¦ | id¦63209457¦BAC¦S_2343614¦
source water 2 | Prevotella_histicola | 栖组织普雷沃菌 | 79/2945323 | 0.0027 | 1 | 3 | 2 | Prevotella | 普雷沃菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.06 | 0.66 | 0.0188 | 0.1906 | - | - | id¦67588339¦BAC¦R_2912654¦ | id¦54869476¦BAC¦S_7805381¦
source water 2 | Prevotella_pallens | 苍白普雷沃菌 | 84/3108774 | 0.0027 | 1 | 2 | 2 | Prevotella | 普雷沃菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.04 | 0.66 | 0.0119 | 0.1906 | - | - | id¦01984445¦BAC¦R_8214264¦ | id¦65342769¦BAC¦S_9539321¦
source water 2 | Prevotella_intermedia | 中间普雷沃菌 | 81/2674180 | 0.003 | 1 | 2 | 1 | Prevotella | 普雷沃菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.05 | 0.66 | 0.0138 | 0.1906 | - | - | id¦75523844¦BAC¦R_3847229¦ | id¦44925120¦BAC¦S_5588591¦
source water 2 | Prevotella_jejuni | 空肠普雷沃菌 | 126/3913016 | 0.0032 | 1 | 3 | 1 | Prevotella | 普雷沃菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.05 | 0.66 | 0.0141 | 0.1906 | - | - | id¦85620277¦BAC¦R_8343336¦ | id¦26457927¦BAC¦S_6206053¦
source water 2 | Prevotella_oulorum | 龈炎普雷沃菌 | 42/2832724 | 0.0015 | 1 | 1 | 1 | Prevotella | 普雷沃菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.02 | 0.66 | 0.0065 | 0.1906 | - | - | id¦23557761¦BAC¦R_1626139¦ | id¦41689517¦BAC¦S_8066850¦
source water 2 | Prevotella_salivae | 唾液普雷沃菌 | 42/3099106 | 0.0014 | 1 | 1 | 1 | Prevotella | 普雷沃菌属 | 32 | 23 | 1 | 1 | 12 | 8 | G- | 0.02 | 0.66 | 0.006 | 0.1906 | - | - | id¦23288787¦BAC¦R_9059536¦ | id¦94593696¦BAC¦S_4324435¦
source water 2 | Aeribacillus_composti | 堆肥气芽胞杆菌 | 168/3778206 | 0.0044 | 1 | 4 | 0 | Aeribacillus | 气芽胞杆菌属 | 26 | 22 | 1 | 0 | 10 | 8 | G+ | 0.07 | 0.41 | 0.0195 | 0.1188 | 1 | 0.51 | id¦02898183¦BAC¦R_8307278¦ | id¦36857853¦BAC¦S_4458063¦
source water 2 | Aeribacillus_pallidus | 苍白气芽胞杆菌 | 794/4089457 | 0.0194 | 1 | 22 | 0 | Aeribacillus | 气芽胞杆菌属 | 26 | 22 | 8 | 0 | 10 | 8 | G+ | 0.34 | 0.41 | 0.0993 | 0.1188 | 1 | 0.86 | id¦17728774¦BAC¦R_0595212¦ | id¦07071783¦BAC¦S_5381751¦
source water 2 | Anaerococcus_nagyae | 纳吉氏厌氧球菌 | 84/1824579 | 0.0046 | 1 | 2 | 1 | Anaerococcus | 厌氧球菌属 | 24 | 22 | 1 | 1 | 9 | 8 | G+ | 0.07 | 0.8 | 0.0202 | 0.233 | - | - | id¦53833902¦BAC¦R_8579025¦ | id¦06526781¦BAC¦S_9279551¦
source water 2 | Anaerococcus_rubeinfantis | 红色婴儿厌氧球菌 | 84/1928970 | 0.0044 | 1 | 2 | 1 | Anaerococcus | 厌氧球菌属 | 24 | 22 | 1 | 1 | 9 | 8 | G+ | 0.07 | 0.8 | 0.0191 | 0.233 | - | - | id¦39715696¦BAC¦R_0615567¦ | id¦92569187¦BAC¦S_8572118¦
source water 2 | Anaerococcus_senegalensis | 塞内加尔厌氧球菌 | 42/1777021 | 0.0024 | 1 | 1 | 1 | Anaerococcus | 厌氧球菌属 | 24 | 22 | 1 | 1 | 9 | 8 | G+ | 0.04 | 0.8 | 0.0104 | 0.233 | - | - | id¦01211711¦BAC¦R_3632460¦ | id¦01392203¦BAC¦S_2132782¦
source water 2 | Comamonas_aquatica | 水生丛毛单胞菌 | 210/3942728 | 0.0053 | 1 | 7 | 3 | Comamonas | 丛毛单胞菌属 | 39 | 21 | 3 | 1 | 14 | 8 | G- | 0.11 | 0.5 | 0.0328 | 0.1441 | 1 | 0.96 | id¦26802777¦BAC¦R_1114359¦ | id¦51095929¦BAC¦S_7965541¦
source water 2 | Comamonas_testosteroni | 睾丸酮丛毛单胞菌 | 210/5687007 | 0.0037 | 1 | 11 | 3 | Comamonas | 丛毛单胞菌属 | 39 | 21 | 4 | 1 | 14 | 8 | G- | 0.12 | 0.5 | 0.0357 | 0.1441 | 1 | 0.61 | id¦03487474¦BAC¦R_7454705¦ | id¦07608799¦BAC¦S_6338317¦
source water 2 | Comamonas_terrigena | 土生丛毛单胞菌 | 122/4710225 | 0.0026 | 1 | 3 | 1 | Comamonas | 丛毛单胞菌属 | 39 | 21 | 1 | 1 | 14 | 8 | G- | 0.04 | 0.5 | 0.0118 | 0.1441 | - | - | id¦55590594¦BAC¦R_6455959¦ | id¦95424253¦BAC¦S_6876733¦
source water 2 | Kocuria_rhizophila | 嗜根库克菌 | 126/2833537 | 0.0044 | 1 | 6 | 3 | Kocuria | 库克菌属 | 29 | 21 | 2 | 1 | 11 | 8 | G+ | 0.13 | 0.61 | 0.0391 | 0.1757 | - | - | id¦67863491¦BAC¦R_6189820¦ | id¦52916262¦BAC¦S_9425461¦
source water 2 | Kocuria_carniphila | 嗜肉库克菌 | 84/3420952 | 0.0025 | 1 | 2 | 1 | Kocuria | 库克菌属 | 29 | 21 | 1 | 1 | 11 | 8 | G+ | 0.04 | 0.61 | 0.0108 | 0.1757 | - | - | id¦91169982¦BAC¦R_1884189¦ | id¦93558742¦BAC¦S_6367316¦
source water 2 | Kocuria_indica | 印度库克菌 | 42/3083405 | 0.0014 | 1 | 1 | 1 | Kocuria | 库克菌属 | 29 | 21 | 1 | 1 | 11 | 8 | G+ | 0.02 | 0.61 | 0.006 | 0.1757 | - | - | id¦53025021¦BAC¦R_2035230¦ | id¦76379113¦BAC¦S_7929307¦
source water 2 | Kocuria_rosea | 玫瑰库克菌 | 168/4018356 | 0.0042 | 1 | 4 | 1 | Kocuria | 库克菌属 | 29 | 21 | 1 | 1 | 11 | 8 | G+ | 0.06 | 0.61 | 0.0184 | 0.1757 | 1 | 0.95 | id¦65484678¦BAC¦R_5470970¦ | id¦98205345¦BAC¦S_4441106¦
source water 2 | Mycolicibacterium_fortuitum | 偶发分枝杆菌 | 208/7094298 | 0.0029 | 1.19 | 6 | 5 | Mycolicibacterium | - | 24 | 20 | 2 | 2 | 9 | 7 | G+ | 0.05 | 0.25 | 0.0156 | 0.0717 | 0.84 | 0.79 | id¦91464418¦BAC¦R_2877155¦ | id¦06002869¦BAC¦S_4684479¦
source water 2 | Mycolicibacterium_gilvum | 黄分枝杆菌 | 210/6433093 | 0.0033 | 1 | 5 | 4 | Mycolicibacterium | - | 24 | 20 | 2 | 1 | 9 | 7 | G+ | 0.05 | 0.25 | 0.0143 | 0.0717 | 1 | 0.96 | id¦15129253¦BAC¦R_6571466¦ | id¦12632911¦BAC¦S_4555052¦
source water 2 | Mycolicibacterium_doricum | 多瑞卡分枝杆菌 | 84/4029398 | 0.0021 | 1 | 2 | 2 | Mycolicibacterium | - | 24 | 20 | 1 | 1 | 9 | 7 | G+ | 0.03 | 0.25 | 0.0092 | 0.0717 | - | - | id¦94863900¦BAC¦R_7992614¦ | id¦72870500¦BAC¦S_0880549¦
source water 2 | Mycolicibacterium_iranicum | 伊朗分枝杆菌 | 42/6125790 | 0.0007 | 1 | 2 | 2 | Mycolicibacterium | - | 24 | 20 | 1 | 1 | 9 | 7 | G+ | 0.02 | 0.25 | 0.006 | 0.0717 | - | - | id¦19939407¦BAC¦R_4191858¦ | id¦55030411¦BAC¦S_3336568¦
source water 2 | Mycolicibacterium_holsaticum | 荷斯坦分枝杆菌 | 42/5750878 | 0.0007 | 1 | 1 | 1 | Mycolicibacterium | - | 24 | 20 | 1 | 1 | 9 | 7 | G+ | 0.01 | 0.25 | 0.0032 | 0.0717 | - | - | id¦43077928¦BAC¦R_7821669¦ | id¦48475665¦BAC¦S_4814422¦
source water 2 | Mycolicibacterium_mucogenicum | 产黏液分枝杆菌 | 84/6376924 | 0.0013 | 1 | 2 | 1 | Mycolicibacterium | - | 24 | 20 | 1 | 1 | 9 | 7 | G+ | 0.02 | 0.25 | 0.0058 | 0.0717 | - | - | id¦32769863¦BAC¦R_6862880¦ | id¦03557975¦BAC¦S_5225457¦
source water 2 | Blautia_wexlerae | 韦氏布劳特菌 | 714/3603672 | 0.0198 | 1 | 20 | 3 | Blautia | 布劳特菌属 | 26 | 19 | 7 | 1 | 10 | 7 | G+ | 0.35 | 0.46 | 0.1024 | 0.1322 | 1 | 0.88 | id¦00753432¦BAC¦R_2716347¦ | id¦08285100¦BAC¦S_8039634¦
source water 2 | Blautia_obeum | 卵形布劳特菌 | 168/3720225 | 0.0045 | 1 | 5 | 0 | Blautia | 布劳特菌属 | 26 | 19 | 2 | 0 | 10 | 7 | G+ | 0.09 | 0.46 | 0.0248 | 0.1322 | 1 | 0.95 | id¦07938846¦BAC¦R_6672880¦ | id¦02059938¦BAC¦S_1407348¦
source water 2 | Chryseobacterium_haifense | 海法金黄杆菌 | 205/2843295 | 0.0072 | 1 | 8 | 6 | Chryseobacterium | 金黄杆菌属 | 32 | 18 | 3 | 2 | 12 | 7 | G- | 0.18 | 0.58 | 0.0519 | 0.1696 | 1 | 0.96 | id¦69559452¦BAC¦R_7437025¦ | id¦30510620¦BAC¦S_1973180¦
source water 2 | Chryseobacterium_bovis | 牛金黄杆菌 | 84/3343737 | 0.0025 | 1 | 2 | 2 | Chryseobacterium | 金黄杆菌属 | 32 | 18 | 1 | 1 | 12 | 7 | G- | 0.04 | 0.58 | 0.011 | 0.1696 | - | - | id¦29365175¦BAC¦R_7341244¦ | id¦03741961¦BAC¦S_1462659¦
source water 2 | Chryseobacterium_hominis | 人型金黄杆菌 | 126/2918756 | 0.0043 | 1 | 4 | 1 | Chryseobacterium | 金黄杆菌属 | 32 | 18 | 1 | 1 | 12 | 7 | G- | 0.09 | 0.58 | 0.0253 | 0.1696 | - | - | id¦83088918¦BAC¦R_0889343¦ | id¦54918380¦BAC¦S_5767828¦
source water 2 | Chryseobacterium_scophthalmum | 比目鱼金黄杆菌 | 42/4447781 | 0.0009 | 1 | 1 | 1 | Chryseobacterium | 金黄杆菌属 | 32 | 18 | 1 | 1 | 12 | 7 | G- | 0.01 | 0.58 | 0.0041 | 0.1696 | - | - | id¦42262376¦BAC¦R_0149633¦ | id¦57939154¦BAC¦S_5682728¦
source water 2 | Chryseobacterium_taklimakanense | 塔拉玛干金黄杆菌 | 42/2764880 | 0.0015 | 1 | 2 | 1 | Chryseobacterium | 金黄杆菌属 | 32 | 18 | 1 | 1 | 12 | 7 | G- | 0.05 | 0.58 | 0.0133 | 0.1696 | - | - | id¦04756579¦BAC¦R_9160412¦ | id¦58889401¦BAC¦S_5928381¦
source water 2 | Deinococcus_reticulitermitis | 散白蚁异常球菌 | 210/3500821 | 0.006 | 1 | 5 | 4 | Deinococcus | 异常球菌属 | 31 | 17 | 2 | 1 | 11 | 6 | G- | 0.09 | 0.55 | 0.0264 | 0.1588 | 1 | 0.61 | id¦40406669¦BAC¦R_2897970¦ | id¦37390314¦BAC¦S_7753674¦
source water 2 | Deinococcus_wulumuqiensis | 乌鲁木齐异常球菌 | 84/3370590 | 0.0025 | 1 | 2 | 2 | Deinococcus | 异常球菌属 | 31 | 17 | 1 | 1 | 11 | 6 | G+ | 0.04 | 0.55 | 0.0109 | 0.1588 | - | - | id¦45997631¦BAC¦R_2304004¦ | id¦36973860¦BAC¦S_3337173¦
source water 2 | Deinococcus_indicus | 印度异常球菌 | 84/4467802 | 0.0019 | 1 | 2 | 1 | Deinococcus | 异常球菌属 | 31 | 17 | 1 | 1 | 11 | 6 | G- | 0.03 | 0.55 | 0.0083 | 0.1588 | - | - | id¦31105983¦BAC¦R_3912584¦ | id¦82179055¦BAC¦S_8899655¦
source water 2 | Deinococcus_murrayi | 墨氏异常球菌 | 118/2760346 | 0.0043 | 1 | 3 | 1 | Deinococcus | 异常球菌属 | 31 | 17 | 1 | 1 | 11 | 6 | G+ | 0.07 | 0.55 | 0.0201 | 0.1588 | - | - | id¦54103382¦BAC¦R_9798077¦ | id¦29292005¦BAC¦S_8889932¦
source water 2 | Nocardioides_glacieisoli | 冰川土类诺卡菌 | 252/4577600 | 0.0055 | 1 | 6 | 3 | Nocardioides | 类诺卡菌属 | 68 | 17 | 2 | 1 | 25 | 6 | G+ | 0.08 | 0.97 | 0.0242 | 0.2813 | 1 | 0.58 | id¦02721284¦BAC¦R_5580083¦ | id¦62401064¦BAC¦S_5054541¦
source water 2 | Nocardioides_daphniae | 水蚤类诺卡菌 | 84/3558816 | 0.0024 | 1 | 2 | 2 | Nocardioides | 类诺卡菌属 | 68 | 17 | 1 | 1 | 25 | 6 | G+ | 0.04 | 0.97 | 0.0104 | 0.2813 | - | - | id¦22532338¦BAC¦R_4104897¦ | id¦76992429¦BAC¦S_2829600¦
source water 2 | Nocardioides_terrigena | 土生类诺卡菌 | 788/4746246 | 0.0166 | 1 | 19 | 2 | Nocardioides | 类诺卡菌属 | 68 | 17 | 7 | 1 | 25 | 6 | G+ | 0.25 | 0.97 | 0.0739 | 0.2813 | 1 | 0.92 | id¦39911082¦BAC¦R_4126507¦ | id¦07876338¦BAC¦S_4794863¦
source water 2 | Nocardioides_currus | 车类诺卡菌 | 203/4534046 | 0.0045 | 1 | 5 | 1 | Nocardioides | 类诺卡菌属 | 68 | 17 | 2 | 1 | 25 | 6 | G+ | 0.07 | 0.97 | 0.0203 | 0.2813 | 1 | 0.96 | id¦24104948¦BAC¦R_3597152¦ | id¦50898883¦BAC¦S_9342488¦
source water 2 | Lactobacillus_rossiae | 罗西氏乳杆菌 | 252/2729298 | 0.0092 | 1 | 8 | 7 | Lactobacillus | 乳杆菌属 | 16 | 16 | 3 | 3 | 6 | 6 | G+ | 0.19 | 0.41 | 0.0541 | 0.1203 | 1 | 0.41 | id¦90234340¦BAC¦R_5024110¦ | id¦85465107¦BAC¦S_4677617¦
source water 2 | Lactobacillus_amylovorus | 食淀粉乳杆菌 | 42/2172769 | 0.0019 | 1 | 1 | 1 | Lactobacillus | 乳杆菌属 | 16 | 16 | 1 | 1 | 6 | 6 | G+ | 0.03 | 0.41 | 0.0085 | 0.1203 | - | - | id¦25337006¦BAC¦R_2239561¦ | id¦21685388¦BAC¦S_0734277¦
source water 2 | Lactobacillus_brevis | 短乳杆菌 | 42/2596074 | 0.0016 | 1 | 1 | 1 | Lactobacillus | 乳杆菌属 | 16 | 16 | 1 | 1 | 6 | 6 | G+ | 0.02 | 0.41 | 0.0071 | 0.1203 | - | - | id¦85751535¦BAC¦R_7847144¦ | id¦14154584¦BAC¦S_9233101¦
source water 2 | Lactobacillus_jensenii | 詹氏乳杆菌 | 42/1672949 | 0.0025 | 1 | 1 | 1 | Lactobacillus | 乳杆菌属 | 16 | 16 | 1 | 1 | 6 | 6 | G+ | 0.04 | 0.41 | 0.011 | 0.1203 | - | - | id¦45117717¦BAC¦R_3304881¦ | id¦68194431¦BAC¦S_8627669¦
source water 2 | Lactobacillus_panis | 面包乳杆菌 | 42/2043735 | 0.0021 | 1 | 1 | 1 | Lactobacillus | 乳杆菌属 | 16 | 16 | 1 | 1 | 6 | 6 | G+ | 0.03 | 0.41 | 0.009 | 0.1203 | - | - | id¦64834460¦BAC¦R_0199665¦ | id¦06202747¦BAC¦S_7994342¦
source water 2 | Lactobacillus_plantarum | 植物乳杆菌 | 75/3360741 | 0.0022 | 1.12 | 2 | 1 | Lactobacillus | 乳杆菌属 | 16 | 16 | 1 | 1 | 6 | 6 | G+ | 0.04 | 0.41 | 0.011 | 0.1203 | - | - | id¦92413120¦BAC¦R_6434239¦ | id¦13090707¦BAC¦S_3244468¦
source water 2 | Microbacterium_lacticum | 乳微杆菌 | 126/3086984 | 0.0041 | 1 | 3 | 2 | Microbacterium | 微杆菌属 | 27 | 16 | 1 | 1 | 10 | 6 | G+ | 0.06 | 0.48 | 0.0179 | 0.1404 | - | - | id¦14600822¦BAC¦R_9664189¦ | id¦53363608¦BAC¦S_7455129¦
source water 2 | Microbacterium_oxydans | 氧化微杆菌 | 84/3906890 | 0.0022 | 1 | 3 | 2 | Microbacterium | 微杆菌属 | 27 | 16 | 1 | 1 | 10 | 6 | G+ | 0.05 | 0.48 | 0.0142 | 0.1404 | - | - | id¦30332603¦BAC¦R_6234895¦ | id¦00262846¦BAC¦S_3058741¦
source water 2 | Microbacterium_enclense | 印国化室微杆菌 | 84/3665072 | 0.0023 | 1 | 3 | 1 | Microbacterium | 微杆菌属 | 27 | 16 | 1 | 1 | 10 | 6 | G+ | 0.05 | 0.48 | 0.0151 | 0.1404 | - | - | id¦52900106¦BAC¦R_7494739¦ | id¦98862669¦BAC¦S_2764378¦
source water 2 | Microbacterium_hominis | 人型微杆菌 | 84/3624793 | 0.0023 | 1 | 2 | 1 | Microbacterium | 微杆菌属 | 27 | 16 | 1 | 1 | 10 | 6 | G+ | 0.04 | 0.48 | 0.0102 | 0.1404 | - | - | id¦66121834¦BAC¦R_6456580¦ | id¦37751729¦BAC¦S_7803513¦
source water 2 | Microbacterium_ketosireducens | 酮糖微杆菌 | 42/3921668 | 0.0011 | 1 | 1 | 1 | Microbacterium | 微杆菌属 | 27 | 16 | 1 | 1 | 10 | 6 | G+ | 0.02 | 0.48 | 0.0047 | 0.1404 | - | - | id¦37338140¦BAC¦R_0198639¦ | id¦01230329¦BAC¦S_3080327¦
source water 2 | Microbacterium_oleivorans | 食石油微杆菌 | 79/2974062 | 0.0027 | 1 | 2 | 1 | Microbacterium | 微杆菌属 | 27 | 16 | 1 | 1 | 10 | 6 | G+ | 0.04 | 0.48 | 0.0124 | 0.1404 | - | - | id¦77745666¦BAC¦R_7117952¦ | id¦48841872¦BAC¦S_7615862¦
source water 2 | Microbacterium_profundi | 深海中微杆菌 | 39/3366821 | 0.0012 | 1 | 1 | 1 | Microbacterium | 微杆菌属 | 27 | 16 | 1 | 1 | 10 | 6 | G+ | 0.02 | 0.48 | 0.0055 | 0.1404 | - | - | id¦85101796¦BAC¦R_9579382¦ | id¦84353934¦BAC¦S_3360779¦
source water 2 | [Enterobacter]_lignolyticus | - | 42/4814049 | 0.0009 | 1 | 1 | 0 | Pluralibacter | 多源杆菌属 | 21 | 16 | 1 | 0 | 8 | 6 | G- | 0.01 | 0.24 | 0.0038 | 0.0691 | - | - | id¦86340968¦BAC¦R_4240737¦ | id¦95776159¦BAC¦S_8793425¦
source water 2 | Bosea_vaviloviae | - | 243/5594195 | 0.0043 | 1 | 9 | 3 | Bosea | - | 31 | 14 | 3 | 1 | 11 | 5 | G- | 0.1 | 0.34 | 0.0297 | 0.0997 | 1 | 0.92 | id¦46673548¦BAC¦R_0213020¦ | id¦50788255¦BAC¦S_7961384¦
source water 2 | Bosea_robiniae | - | 168/5279303 | 0.0032 | 1 | 4 | 2 | Bosea | - | 31 | 14 | 1 | 1 | 11 | 5 | G- | 0.05 | 0.34 | 0.014 | 0.0997 | 1 | 0.95 | id¦70725981¦BAC¦R_6584976¦ | id¦47178715¦BAC¦S_4067081¦
source water 2 | Brevibacterium_epidermidis | 表皮短杆菌 | 252/3703501 | 0.0068 | 1 | 7 | 4 | Brevibacterium | 短杆菌属 | 17 | 14 | 3 | 1 | 6 | 5 | G+ | 0.12 | 0.29 | 0.0349 | 0.0845 | 1 | 0.58 | id¦57900119¦BAC¦R_6085594¦ | id¦48094664¦BAC¦S_4579775¦
source water 2 | Brevibacterium_linens | 扩展短杆菌 | 84/3862244 | 0.0022 | 1 | 4 | 2 | Brevibacterium | 短杆菌属 | 17 | 14 | 1 | 1 | 6 | 5 | G+ | 0.07 | 0.29 | 0.0191 | 0.0845 | - | - | id¦64086172¦BAC¦R_1951608¦ | id¦43650447¦BAC¦S_6177197¦
source water 2 | Paraburkholderia_tropica | 热带副伯克霍尔德菌 | 374/8824402 | 0.0042 | 1.01 | 10 | 6 | Paraburkholderia | 副伯克霍尔德菌属 | 21 | 13 | 4 | 2 | 8 | 5 | G- | 0.07 | 0.15 | 0.0209 | 0.044 | 0.99 | 0.77 | id¦64701640¦BAC¦R_8200055¦ | id¦86892980¦BAC¦S_1168221¦
source water 2 | Paraburkholderia_xenovorans | 食异生素副伯克霍尔德菌 | 84/9731158 | 0.0009 | 1 | 2 | 1 | Paraburkholderia | 副伯克霍尔德菌属 | 21 | 13 | 1 | 1 | 8 | 5 | G- | 0.01 | 0.15 | 0.0038 | 0.044 | - | - | id¦12944955¦BAC¦R_4244607¦ | id¦10375732¦BAC¦S_5339478¦
source water 2 | Thermincola_potens | - | 326/3157416 | 0.0103 | 1 | 8 | 3 | Thermincola | - | 15 | 13 | 3 | 1 | 6 | 5 | G+ | 0.16 | 0.3 | 0.0468 | 0.0876 | 1 | 0.99 | id¦41540544¦BAC¦R_9252910¦ | id¦74426736¦BAC¦S_6595292¦
source water 2 | Thermincola_ferriacetica | - | 294/3168320 | 0.0093 | 1 | 7 | 2 | Thermincola | - | 15 | 13 | 3 | 1 | 6 | 5 | G+ | 0.14 | 0.3 | 0.0408 | 0.0876 | 1 | 0.98 | id¦18472695¦BAC¦R_8367467¦ | id¦25563019¦BAC¦S_5182817¦
source water 2 | Actinomyces_graevenitzii | 格雷文尼放线菌 | 84/2084268 | 0.004 | 1 | 3 | 3 | Actinomyces | 放线菌属 | 12 | 12 | 1 | 1 | 4 | 4 | G+ | 0.09 | 0.28 | 0.0266 | 0.081 | - | - | id¦96213277¦BAC¦R_5766226¦ | id¦89962810¦BAC¦S_3814609¦
source water 2 | Actinomyces_massiliensis | 马赛放线菌 | 42/3399686 | 0.0012 | 1 | 1 | 1 | Actinomyces | 放线菌属 | 12 | 12 | 1 | 1 | 4 | 4 | G+ | 0.02 | 0.28 | 0.0054 | 0.081 | - | - | id¦30593686¦BAC¦R_8842019¦ | id¦67888113¦BAC¦S_8118948¦
source water 2 | Actinomyces_naeslundii | 内氏放线菌 | 42/3160965 | 0.0013 | 1 | 2 | 1 | Actinomyces | 放线菌属 | 12 | 12 | 1 | 1 | 4 | 4 | G+ | 0.04 | 0.28 | 0.0117 | 0.081 | - | - | id¦65055208¦BAC¦R_1197092¦ | id¦63177970¦BAC¦S_7167271¦
source water 2 | Actinomyces_oris | 口腔放线菌 | 42/3280778 | 0.0013 | 1 | 3 | 1 | Actinomyces | 放线菌属 | 12 | 12 | 1 | 1 | 4 | 4 | G+ | 0.06 | 0.28 | 0.0169 | 0.081 | - | - | id¦22869972¦BAC¦R_5567952¦ | id¦19392096¦BAC¦S_9396489¦
source water 2 | Actinomyces_provencensis | 普罗旺斯放线菌 | 42/3302313 | 0.0013 | 1 | 1 | 1 | Actinomyces | 放线菌属 | 12 | 12 | 1 | 1 | 4 | 4 | G+ | 0.02 | 0.28 | 0.0056 | 0.081 | - | - | id¦40086352¦BAC¦R_0089101¦ | id¦04253565¦BAC¦S_7318875¦
source water 2 | Bifidobacterium_thermacidophilum | 高温双歧杆菌 | 252/2233142 | 0.0113 | 1 | 6 | 1 | Bifidobacterium | 双歧杆菌属 | 16 | 12 | 2 | 1 | 6 | 4 | G+ | 0.17 | 0.44 | 0.0496 | 0.1282 | 1 | 0.92 | id¦83756996¦BAC¦R_4722380¦ | id¦60159582¦BAC¦S_4661531¦
source water 2 | Bifidobacterium_thermophilum | 嗜热双歧杆菌 | 268/2220596 | 0.0121 | 1.09 | 7 | 1 | Bifidobacterium | 双歧杆菌属 | 16 | 12 | 3 | 1 | 6 | 4 | G+ | 0.2 | 0.44 | 0.0582 | 0.1282 | 0.92 | 0.54 | id¦68928459¦BAC¦R_3064630¦ | id¦70246840¦BAC¦S_9999378¦
source water 2 | Bradyrhizobium_sp._BTAi1 | 慢生根瘤菌BTAi1 | 126/8264687 | 0.0015 | 1 | 3 | 2 | Bradyrhizobium | 慢生根瘤菌属 | 28 | 12 | 1 | 1 | 10 | 4 | G- | 0.02 | 0.22 | 0.0067 | 0.0627 | - | - | id¦39765305¦BAC¦R_9966658¦ | id¦83252480¦BAC¦S_8337294¦
source water 2 | Bradyrhizobium_macuxiense | 慢生根瘤菌* | 42/8820085 | 0.0005 | 1 | 1 | 1 | Bradyrhizobium | 慢生根瘤菌属 | 28 | 12 | 1 | 1 | 10 | 4 | G- | 0.01 | 0.22 | 0.0021 | 0.0627 | - | - | id¦97640670¦BAC¦R_7643903¦ | id¦93927739¦BAC¦S_9585826¦
source water 2 | Janibacter_melonis | 柠檬两面神菌 | 294/3196914 | 0.0092 | 1 | 8 | 5 | Janibacter | 两面神菌属 | 19 | 12 | 3 | 2 | 7 | 4 | G+ | 0.16 | 0.37 | 0.0462 | 0.1081 | 1 | 0.98 | id¦18682463¦BAC¦R_0607306¦ | id¦41852030¦BAC¦S_1692010¦
source water 2 | Janibacter_anophelis | 按蚊中肠两面神菌 | 126/3304531 | 0.0038 | 1 | 3 | 3 | Janibacter | 两面神菌属 | 19 | 12 | 1 | 1 | 7 | 4 | G+ | 0.06 | 0.37 | 0.0168 | 0.1081 | - | - | id¦68841165¦BAC¦R_3054691¦ | id¦71032871¦BAC¦S_7051218¦
source water 2 | Janibacter_hoylei | 霍伊尔两面神菌 | 168/3134151 | 0.0054 | 1 | 4 | 2 | Janibacter | 两面神菌属 | 19 | 12 | 1 | 1 | 7 | 4 | G+ | 0.08 | 0.37 | 0.0236 | 0.1081 | 1 | 0.95 | id¦63479072¦BAC¦R_7127218¦ | id¦89291528¦BAC¦S_1018326¦
source water 2 | Sphingobium_yanoikuyae | 矢野口鞘脂菌 | 120/5346022 | 0.0022 | 1 | 5 | 3 | Sphingobium | 鞘脂菌属 | 26 | 12 | 2 | 1 | 10 | 4 | G- | 0.06 | 0.36 | 0.0173 | 0.1034 | - | - | id¦44657755¦BAC¦R_6702965¦ | id¦75042391¦BAC¦S_3739105¦
source water 2 | Sphingobium_limneticum | 湖泊鞘脂菌 | 42/5177571 | 0.0008 | 1 | 1 | 1 | Sphingobium | 鞘脂菌属 | 26 | 12 | 1 | 1 | 10 | 4 | G- | 0.01 | 0.36 | 0.0036 | 0.1034 | - | - | id¦44093913¦BAC¦R_7142348¦ | id¦22758440¦BAC¦S_8006728¦
source water 2 | Sphingobium_phenoxybenzoativorans | 食苯氧基苯甲酸酯鞘脂菌 | 84/5030596 | 0.0017 | 1 | 2 | 1 | Sphingobium | 鞘脂菌属 | 26 | 12 | 1 | 1 | 10 | 4 | G- | 0.03 | 0.36 | 0.0073 | 0.1034 | - | - | id¦34235902¦BAC¦R_7882573¦ | id¦55001105¦BAC¦S_1765250¦
source water 2 | Sphingobium_xenophagum | 噬异物鞘脂菌 | 126/3860193 | 0.0033 | 1 | 4 | 1 | Sphingobium | 鞘脂菌属 | 26 | 12 | 1 | 1 | 10 | 4 | G- | 0.07 | 0.36 | 0.0191 | 0.1034 | - | - | id¦69004752¦BAC¦R_4181985¦ | id¦63296447¦BAC¦S_5884031¦
source water 2 | Defluviimonas_denitrificans | - | 1873/4108205 | 0.0456 | 1 | 46 | 8 | Defluviimonas | - | 54 | 11 | 17 | 3 | 20 | 4 | G- | 0.71 | 0.82 | 0.2066 | 0.2392 | 1 | 0.98 | id¦86844162¦BAC¦R_7376025¦ | id¦86255838¦BAC¦S_6679778¦
source water 2 | Defluviimonas_alba | - | 210/4738298 | 0.0044 | 1 | 5 | 2 | Defluviimonas | - | 54 | 11 | 2 | 1 | 20 | 4 | G- | 0.07 | 0.82 | 0.0195 | 0.2392 | 1 | 0 | id¦77526846¦BAC¦R_5126928¦ | id¦41694806¦BAC¦S_9001828¦
source water 2 | Neisseria_elongata | 长奈瑟菌 | 119/2397276 | 0.005 | 1 | 3 | 1 | Neisseria | 奈瑟菌属 | 24 | 11 | 1 | 1 | 9 | 4 | G- | 0.08 | 0.65 | 0.0231 | 0.1895 | - | - | id¦27066780¦BAC¦R_1630041¦ | id¦31575720¦BAC¦S_5376443¦
source water 2 | Neisseria_cinerea | 灰色奈瑟菌 | 42/1900580 | 0.0022 | 1 | 2 | 0 | Neisseria | 奈瑟菌属 | 24 | 11 | 1 | 0 | 9 | 4 | G- | 0.07 | 0.65 | 0.0194 | 0.1895 | - | - | id¦00205397¦BAC¦R_6796403¦ | id¦90163532¦BAC¦S_9550791¦
source water 2 | Delftia_acidovorans | 食酸代尔夫特菌 | 378/6767514 | 0.0056 | 1 | 11 | 1 | Delftia | 代尔夫特菌属 | 22 | 10 | 4 | 1 | 8 | 4 | G- | 0.1 | 0.21 | 0.03 | 0.0598 | 1 | 1 | id¦36837317¦BAC¦R_0227107¦ | id¦25585541¦BAC¦S_9184453¦
source water 2 | Delftia_lacustris | 池生代尔夫特菌 | 210/6942149 | 0.003 | 1 | 5 | 0 | Delftia | 代尔夫特菌属 | 22 | 10 | 2 | 0 | 8 | 4 | G- | 0.05 | 0.21 | 0.0133 | 0.0598 | 1 | 0.61 | id¦94839633¦BAC¦R_5635591¦ | id¦47439179¦BAC¦S_1017267¦
source water 2 | Enterococcus_cecorum | 盲肠肠球菌 | 168/2273393 | 0.0074 | 1 | 5 | 5 | Enterococcus | 肠球菌属 | 10 | 10 | 2 | 2 | 4 | 4 | G+ | 0.14 | 0.23 | 0.0406 | 0.0666 | 1 | 0.51 | id¦30622239¦BAC¦R_8293228¦ | id¦23097671¦BAC¦S_8975236¦
source water 2 | Enterococcus_avium | 鸟肠球菌 | 84/4794392 | 0.0018 | 1 | 2 | 2 | Enterococcus | 肠球菌属 | 10 | 10 | 1 | 1 | 4 | 4 | G+ | 0.03 | 0.23 | 0.0077 | 0.0666 | - | - | id¦21753809¦BAC¦R_9098037¦ | id¦54119988¦BAC¦S_1446168¦
source water 2 | Enterococcus_aquimarinus | 海洋肠球菌 | 42/2510134 | 0.0017 | 1 | 1 | 1 | Enterococcus | 肠球菌属 | 10 | 10 | 1 | 1 | 4 | 4 | G+ | 0.03 | 0.23 | 0.0074 | 0.0666 | - | - | id¦31127433¦BAC¦R_2732927¦ | id¦60342030¦BAC¦S_2556737¦
source water 2 | Enterococcus_faecium | 屎肠球菌 | 42/3130373 | 0.0013 | 1 | 1 | 1 | Enterococcus | 肠球菌属 | 10 | 10 | 1 | 1 | 4 | 4 | G+ | 0.02 | 0.23 | 0.0059 | 0.0666 | - | - | id¦66505615¦BAC¦R_7132705¦ | id¦66275801¦BAC¦S_2655548¦
source water 2 | Achromobacter_insuavis | 罕见无色杆菌 | 294/6884738 | 0.0043 | 1 | 8 | 3 | Achromobacter | 无色杆菌属 | 17 | 9 | 3 | 1 | 6 | 3 | G- | 0.07 | 0.16 | 0.0214 | 0.0468 | 1 | 0.87 | id¦25177847¦BAC¦R_7963028¦ | id¦82949178¦BAC¦S_2877341¦
source water 2 | Achromobacter_aegrifaciens | 致病无色杆菌 | 42/6943014 | 0.0006 | 1 | 1 | 0 | Achromobacter | 无色杆菌属 | 17 | 9 | 1 | 0 | 6 | 3 | G- | 0.01 | 0.16 | 0.0027 | 0.0468 | - | - | id¦20898107¦BAC¦R_6891420¦ | id¦11175142¦BAC¦S_2866350¦
source water 2 | Mycolicibacter_arupensis | 阿普罗分枝杆菌 | 294/5011158 | 0.0059 | 1 | 7 | 7 | Mycolicibacter | - | 9 | 9 | 3 | 3 | 3 | 3 | G+ | 0.09 | 0.12 | 0.0258 | 0.034 | 1 | 0.98 | id¦88115789¦BAC¦R_2307858¦ | id¦35420916¦BAC¦S_1939591¦
source water 2 | Mycolicibacter_longobardus | 伦巴第分枝杆菌 | 42/4812827 | 0.0009 | 1 | 1 | 0 | Mycolicibacter | - | 9 | 9 | 1 | 0 | 3 | 3 | G+ | 0.01 | 0.12 | 0.0038 | 0.034 | - | - | id¦56109480¦BAC¦R_0742010¦ | id¦49607758¦BAC¦S_4467127¦
source water 2 | Ochrobactrum_lupini | 羽扇豆苍白杆菌 | 84/5579192 | 0.0015 | 1 | 2 | 1 | Ochrobactrum | 苍白杆菌属 | 13 | 9 | 1 | 1 | 5 | 3 | G- | 0.02 | 0.16 | 0.0066 | 0.0473 | - | - | id¦09782231¦BAC¦R_5119006¦ | id¦10568656¦BAC¦S_5029951¦
source water 2 | Ochrobactrum_anthropi | 人苍白杆菌 | 122/4853933 | 0.0025 | 1.03 | 6 | 0 | Ochrobactrum | 苍白杆菌属 | 13 | 9 | 2 | 0 | 5 | 3 | G- | 0.08 | 0.16 | 0.0228 | 0.0473 | - | - | id¦01718978¦BAC¦R_6282566¦ | id¦63001808¦BAC¦S_3213786¦
source water 2 | Serratia_marcescens | 黏质沙雷菌 | 252/5221717 | 0.0048 | 1 | 6 | 3 | Serratia | 沙雷菌属 | 12 | 9 | 2 | 1 | 4 | 3 | G- | 0.07 | 0.14 | 0.0212 | 0.0421 | 1 | 1 | id¦20564968¦BAC¦R_6312885¦ | id¦90467460¦BAC¦S_4152514¦
source water 2 | Serratia_grimesii | 格氏沙雷菌 | 42/5089920 | 0.0008 | 1 | 1 | 1 | Serratia | 沙雷菌属 | 12 | 9 | 1 | 1 | 4 | 3 | G- | 0.01 | 0.14 | 0.0036 | 0.0421 | - | - | id¦55210534¦BAC¦R_7403729¦ | id¦01050872¦BAC¦S_2780151¦
source water 2 | Serratia_liquefaciens | 液化沙雷菌 | 42/5521835 | 0.0008 | 1 | 1 | 1 | Serratia | 沙雷菌属 | 12 | 9 | 1 | 1 | 4 | 3 | G- | 0.01 | 0.14 | 0.0033 | 0.0421 | - | - | id¦72054082¦BAC¦R_1560103¦ | id¦71392862¦BAC¦S_3382172¦
source water 2 | Alcaligenes_faecalis | 粪产碱杆菌 | 210/4204035 | 0.005 | 1 | 8 | 4 | Alcaligenes | 产碱杆菌属 | 10 | 8 | 3 | 1 | 4 | 3 | G- | 0.12 | 0.15 | 0.0351 | 0.0438 | 1 | 0.61 | id¦64663368¦BAC¦R_5598986¦ | id¦80235307¦BAC¦S_6661316¦
source water 2 | Alcaligenes_aquatilis | 水生产碱杆菌 | 42/4219621 | 0.001 | 1 | 2 | 0 | Alcaligenes | 产碱杆菌属 | 10 | 8 | 1 | 0 | 4 | 3 | G- | 0.03 | 0.15 | 0.0087 | 0.0438 | - | - | id¦08839294¦BAC¦R_8966948¦ | id¦06110550¦BAC¦S_5438702¦
source water 2 | Aquabacterium_olei | 油水小杆菌 | 252/3890087 | 0.0065 | 1 | 6 | 3 | Aquabacterium | 水小杆菌属 | 18 | 8 | 2 | 1 | 7 | 3 | G- | 0.1 | 0.28 | 0.0285 | 0.081 | 1 | 0.79 | id¦82117975¦BAC¦R_1965251¦ | id¦99573920¦BAC¦S_3278383¦
source water 2 | Aquabacterium_commune | 普通水小杆菌 | 165/4204703 | 0.0039 | 1 | 4 | 1 | Aquabacterium | 水小杆菌属 | 18 | 8 | 1 | 1 | 7 | 3 | G- | 0.06 | 0.28 | 0.0176 | 0.081 | 1 | 0.51 | id¦72311672¦BAC¦R_0300836¦ | id¦14819391¦BAC¦S_3311435¦
source water 2 | Aquabacterium_parvum | 细小水小杆菌 | 168/4430728 | 0.0038 | 1 | 4 | 1 | Aquabacterium | 水小杆菌属 | 18 | 8 | 1 | 1 | 7 | 3 | G- | 0.06 | 0.28 | 0.0167 | 0.081 | 1 | 0.63 | id¦66830988¦BAC¦R_1243795¦ | id¦84447872¦BAC¦S_7840726¦
source water 2 | Methylobacterium_brachiatum | 分枝甲基杆菌 | 126/5805468 | 0.0022 | 1 | 3 | 1 | Methylobacterium | 甲基杆菌属 | 12 | 8 | 1 | 1 | 4 | 3 | G- | 0.03 | 0.12 | 0.0095 | 0.0353 | - | - | id¦03581949¦BAC¦R_4286190¦ | id¦88549676¦BAC¦S_7434564¦
source water 2 | Methylobacterium_radiotolerans | 耐辐射甲基杆菌 | 42/6077833 | 0.0007 | 1 | 1 | 1 | Methylobacterium | 甲基杆菌属 | 12 | 8 | 1 | 1 | 4 | 3 | G- | 0.01 | 0.12 | 0.003 | 0.0353 | - | - | id¦04941597¦BAC¦R_1301051¦ | id¦93955112¦BAC¦S_7202747¦
source water 2 | Sphingopyxis_alaskensis | 阿拉斯加鞘氨醇盒菌 | 42/3345170 | 0.0013 | 1 | 1 | 1 | Sphingopyxis | 鞘氨醇盒菌属 | 19 | 8 | 1 | 1 | 7 | 3 | G- | 0.02 | 0.27 | 0.0055 | 0.0794 | - | - | id¦54999803¦BAC¦R_2980684¦ | id¦59642288¦BAC¦S_6244736¦
source water 2 | Sphingopyxis_bauzanensis | 博尔扎诺鞘氨醇盒菌 | 84/4256660 | 0.002 | 1 | 2 | 1 | Sphingopyxis | 鞘氨醇盒菌属 | 19 | 8 | 1 | 1 | 7 | 3 | G- | 0.03 | 0.27 | 0.0087 | 0.0794 | - | - | id¦76070959¦BAC¦R_0161901¦ | id¦31625145¦BAC¦S_5222225¦
source water 2 | Sphingopyxis_fribergensis | 弗莱贝格鞘氨醇盒菌 | 168/4993584 | 0.0034 | 1 | 4 | 1 | Sphingopyxis | 鞘氨醇盒菌属 | 19 | 8 | 1 | 1 | 7 | 3 | G- | 0.05 | 0.27 | 0.0148 | 0.0794 | 1 | 0.63 | id¦97203490¦BAC¦R_0140653¦ | id¦47458060¦BAC¦S_3204916¦
source water 2 | Sphingopyxis_terrae | 土地鞘氨醇盒菌 | 84/4081023 | 0.0021 | 1 | 2 | 1 | Sphingopyxis | 鞘氨醇盒菌属 | 19 | 8 | 1 | 1 | 7 | 3 | G- | 0.03 | 0.27 | 0.009 | 0.0794 | - | - | id¦68336737¦BAC¦R_1703632¦ | id¦23017559¦BAC¦S_0091833¦
source water 2 | Sphingopyxis_witflariensis | 威特弗拉里亚鞘氨醇盒菌 | 84/4307040 | 0.002 | 1 | 2 | 1 | Sphingopyxis | 鞘氨醇盒菌属 | 19 | 8 | 1 | 1 | 7 | 3 | G- | 0.03 | 0.27 | 0.0086 | 0.0794 | - | - | id¦16077940¦BAC¦R_8936692¦ | id¦06494415¦BAC¦S_2025423¦
source water 2 | Carboxydocella_sporoproducens | - | 84/2579744 | 0.0033 | 1 | 2 | 0 | Carboxydocella | - | 8 | 7 | 1 | 0 | 3 | 3 | G+ | 0.05 | 0.19 | 0.0143 | 0.0555 | - | - | id¦50980074¦BAC¦R_1547505¦ | id¦02123824¦BAC¦S_0730841¦
source water 2 | Carboxydocella_thermautotrophica | - | 252/2690058 | 0.0094 | 1 | 6 | 0 | Carboxydocella | - | 8 | 7 | 2 | 0 | 3 | 3 | G+ | 0.14 | 0.19 | 0.0412 | 0.0555 | 1 | 0.41 | id¦92121192¦BAC¦R_6961754¦ | id¦89729342¦BAC¦S_4485682¦
source water 2 | Cloacibacterium_normanense | - | 294/2759562 | 0.0107 | 1 | 7 | 7 | Cloacibacterium | - | 7 | 7 | 3 | 3 | 3 | 3 | G- | 0.16 | 0.16 | 0.0468 | 0.0468 | 1 | 0.62 | id¦08036817¦BAC¦R_0859119¦ | id¦36590735¦BAC¦S_8513847¦
source water 2 | Rhizobium_pusense | 普萨根瘤菌 | 168/5804542 | 0.0029 | 1 | 5 | 5 | Rhizobium | 根瘤菌属 | 26 | 7 | 2 | 2 | 10 | 3 | G- | 0.05 | 0.28 | 0.0159 | 0.081 | 1 | 0.95 | id¦43196479¦BAC¦R_7772076¦ | id¦54701733¦BAC¦S_2580134¦
source water 2 | Rhizobium_alamii | 阿氏根瘤菌 | 34/7396009 | 0.0005 | 1 | 1 | 0 | Rhizobium | 根瘤菌属 | 26 | 7 | 1 | 0 | 10 | 3 | G- | 0.01 | 0.28 | 0.0025 | 0.081 | - | - | id¦20275857¦BAC¦R_3566283¦ | id¦06312991¦BAC¦S_8986461¦
source water 2 | Thermomonas_fusca | - | 573/3149698 | 0.0182 | 1 | 17 | 4 | Thermomonas | - | 28 | 7 | 6 | 1 | 10 | 3 | G- | 0.34 | 0.62 | 0.0996 | 0.1797 | 1 | 0.97 | id¦36115578¦BAC¦R_4714769¦ | id¦43242032¦BAC¦S_7806127¦
source water 2 | Thermomonas_hydrothermalis | - | 161/2445440 | 0.0066 | 1 | 4 | 1 | Thermomonas | - | 28 | 7 | 1 | 1 | 10 | 3 | G- | 0.1 | 0.62 | 0.0302 | 0.1797 | 1 | 0.95 | id¦16592060¦BAC¦R_9879087¦ | id¦49385334¦BAC¦S_0168126¦
source water 2 | Veillonella_parvula | 小韦荣球菌 | 168/2178518 | 0.0077 | 1 | 4 | 3 | Veillonella | 韦荣球菌属 | 10 | 7 | 1 | 1 | 4 | 3 | G- | 0.12 | 0.29 | 0.0339 | 0.0856 | 1 | 0.51 | id¦45550624¦BAC¦R_8006035¦ | id¦39606067¦BAC¦S_3266782¦
source water 2 | Veillonella_atypica | 非典型韦荣球菌 | 42/2046828 | 0.0021 | 1 | 2 | 1 | Veillonella | 韦荣球菌属 | 10 | 7 | 1 | 1 | 4 | 3 | G- | 0.06 | 0.29 | 0.018 | 0.0856 | - | - | id¦89814454¦BAC¦R_7656789¦ | id¦89315361¦BAC¦S_5539862¦
source water 2 | Acetobacter_orientalis | 东方醋杆菌 | 84/2727847 | 0.0031 | 1 | 2 | 2 | Acetobacter | 醋杆菌属 | 23 | 6 | 1 | 1 | 8 | 2 | G- | 0.05 | 0.47 | 0.0135 | 0.1368 | - | - | id¦16314273¦BAC¦R_9962676¦ | id¦92742917¦BAC¦S_2078064¦
source water 2 | Acetobacter_cerevisiae | 酿酒醋杆菌 | 34/3319016 | 0.001 | 1 | 1 | 0 | Acetobacter | 醋杆菌属 | 23 | 6 | 1 | 0 | 8 | 2 | G- | 0.02 | 0.47 | 0.0056 | 0.1368 | - | - | id¦06834493¦BAC¦R_1991744¦ | id¦15544541¦BAC¦S_5836458¦
source water 2 | Clostridium_tyrobutyricum | 酪丁酸梭菌 | 126/3158744 | 0.004 | 1 | 3 | 3 | Clostridium | 梭菌属 | 6 | 6 | 1 | 1 | 2 | 2 | G+ | 0.06 | 0.11 | 0.0175 | 0.0305 | - | - | id¦73069608¦BAC¦R_8565581¦ | id¦51020468¦BAC¦S_8482854¦
source water 2 | Clostridium_formicaceticum | 甲酸乙酸梭菌 | 42/4586755 | 0.0009 | 1 | 1 | 1 | Clostridium | 梭菌属 | 6 | 6 | 1 | 1 | 2 | 2 | G- | 0.01 | 0.11 | 0.004 | 0.0305 | - | - | id¦93107911¦BAC¦R_7755738¦ | id¦60932457¦BAC¦S_7744335¦
source water 2 | Clostridium_kluyveri | 克氏梭菌 | 42/4454353 | 0.0009 | 1 | 1 | 1 | Clostridium | 梭菌属 | 6 | 6 | 1 | 1 | 2 | 2 | G+ | 0.01 | 0.11 | 0.0041 | 0.0305 | - | - | id¦55811145¦BAC¦R_0757735¦ | id¦10339813¦BAC¦S_9691483¦
source water 2 | Clostridium_luticellarii | 泥窖梭菌 | 42/3748471 | 0.0011 | 1 | 1 | 1 | Clostridium | 梭菌属 | 6 | 6 | 1 | 1 | 2 | 2 | G+ | 0.02 | 0.11 | 0.0049 | 0.0305 | - | - | id¦92422059¦BAC¦R_3073159¦ | id¦91932220¦BAC¦S_7012446¦
source water 2 | Klebsiella_huaxiensis | 华西克雷伯菌 | 42/6183608 | 0.0007 | 1 | 1 | 1 | Klebsiella | 克雷伯菌属 | 11 | 6 | 1 | 1 | 4 | 2 | G- | 0.01 | 0.12 | 0.003 | 0.0342 | - | - | id¦56772403¦BAC¦R_8249420¦ | id¦46778667¦BAC¦S_0080008¦
source water 2 | Klebsiella_michiganensis | 密歇根克雷伯菌 | 126/5932766 | 0.0021 | 1 | 3 | 1 | Klebsiella | 克雷伯菌属 | 11 | 6 | 1 | 1 | 4 | 2 | G- | 0.03 | 0.12 | 0.0093 | 0.0342 | - | - | id¦02412263¦BAC¦R_9241077¦ | id¦36888060¦BAC¦S_4711965¦
source water 2 | Massilia_timonae | 蒂莫内马赛菌 | 168/5969261 | 0.0028 | 1 | 5 | 2 | Massilia | 马赛菌属 | 16 | 6 | 2 | 1 | 6 | 2 | G- | 0.05 | 0.16 | 0.0155 | 0.0471 | 1 | 0.95 | id¦76439820¦BAC¦R_2895393¦ | id¦11744690¦BAC¦S_7322272¦
source water 2 | Massilia_alkalitolerans | 耐碱马赛菌 | 40/6112074 | 0.0007 | 1 | 1 | 1 | Massilia | 马赛菌属 | 16 | 6 | 1 | 1 | 6 | 2 | G- | 0.01 | 0.16 | 0.003 | 0.0471 | - | - | id¦26166197¦BAC¦R_4691582¦ | id¦66430614¦BAC¦S_0074171¦
source water 2 | Massilia_oculi | 眼马赛菌 | 42/5844653 | 0.0007 | 1 | 1 | 1 | Massilia | 马赛菌属 | 16 | 6 | 1 | 1 | 6 | 2 | G- | 0.01 | 0.16 | 0.0032 | 0.0471 | - | - | id¦36431455¦BAC¦R_0641487¦ | id¦62004177¦BAC¦S_3698491¦
source water 2 | Pedobacter_caeni | 污水土地杆菌 | 252/7826575 | 0.0032 | 1 | 6 | 6 | Pedobacter | 土地杆菌属 | 6 | 6 | 2 | 2 | 2 | 2 | G- | 0.05 | 0.05 | 0.0141 | 0.0141 | 1 | 0.92 | id¦19020654¦BAC¦R_5929241¦ | id¦72247450¦BAC¦S_7555586¦
source water 2 | Yimella_lutea | - | 252/3533116 | 0.0071 | 1 | 6 | 6 | Yimella | - | 6 | 6 | 2 | 2 | 2 | 2 | G+ | 0.11 | 0.11 | 0.0313 | 0.0313 | 1 | 0.58 | id¦59591354¦BAC¦R_8973304¦ | id¦11089479¦BAC¦S_8817654¦
source water 2 | Citrobacter_braakii | 布氏柠檬酸杆菌 | 42/5445355 | 0.0008 | 1 | 2 | 1 | Citrobacter | 柠檬酸杆菌属 | 8 | 5 | 1 | 1 | 3 | 2 | G- | 0.02 | 0.09 | 0.0068 | 0.0271 | - | - | id¦31236521¦BAC¦R_4009498¦ | id¦53143432¦BAC¦S_1246877¦
source water 2 | Citrobacter_freundii | 弗劳地柠檬酸杆菌 | 126/5744774 | 0.0022 | 1 | 4 | 1 | Citrobacter | 柠檬酸杆菌属 | 8 | 5 | 1 | 1 | 3 | 2 | G- | 0.04 | 0.09 | 0.0128 | 0.0271 | - | - | id¦12214303¦BAC¦R_7359655¦ | id¦23731307¦BAC¦S_8794613¦
source water 2 | Desemzia_incerta | 未定德库菌 | 210/2330968 | 0.009 | 1 | 5 | 5 | Desemzia | 德库菌属 | 5 | 5 | 2 | 2 | 2 | 2 | G+ | 0.14 | 0.14 | 0.0396 | 0.0396 | 1 | 0.96 | id¦97424930¦BAC¦R_8114431¦ | id¦37320224¦BAC¦S_4713580¦
source water 2 | Enterobacter_ludwigii | 路氏肠杆菌 | 84/5369929 | 0.0016 | 1 | 3 | 3 | Enterobacter | 肠杆菌属 | 15 | 5 | 1 | 1 | 6 | 2 | G- | 0.04 | 0.18 | 0.0103 | 0.0537 | - | - | id¦61633621¦BAC¦R_3656195¦ | id¦07335650¦BAC¦S_1068983¦
source water 2 | Enterobacter_mori | 桑树肠杆菌 | 42/4953082 | 0.0008 | 1 | 1 | 1 | Enterobacter | 肠杆菌属 | 15 | 5 | 1 | 1 | 6 | 2 | G- | 0.01 | 0.18 | 0.0037 | 0.0537 | - | - | id¦72385085¦BAC¦R_1992135¦ | id¦50843152¦BAC¦S_3655495¦
source water 2 | Exiguobacterium_profundum | 深海微小杆菌 | 126/2912923 | 0.0043 | 1 | 3 | 3 | Exiguobacterium | 微小杆菌属 | 6 | 5 | 1 | 1 | 2 | 2 | G+ | 0.07 | 0.13 | 0.019 | 0.0366 | - | - | id¦47746070¦BAC¦R_1028800¦ | id¦35574831¦BAC¦S_0059710¦
source water 2 | Exiguobacterium_chiriqhucha | 微小杆菌* | 42/3017018 | 0.0014 | 1 | 1 | 1 | Exiguobacterium | 微小杆菌属 | 6 | 5 | 1 | 1 | 2 | 2 | G+ | 0.02 | 0.13 | 0.0061 | 0.0366 | - | - | id¦86548906¦BAC¦R_3369837¦ | id¦70297486¦BAC¦S_5768228¦
source water 2 | Nesterenkonia_sandarakina | 橙黄涅斯捷连科菌 | 168/3225526 | 0.0052 | 1 | 4 | 4 | Nesterenkonia | 涅斯捷连科菌属 | 5 | 5 | 1 | 1 | 2 | 2 | G+ | 0.08 | 0.1 | 0.0229 | 0.0299 | 1 | 0.51 | id¦08993463¦BAC¦R_9703966¦ | id¦58024038¦BAC¦S_2758699¦
source water 2 | Nesterenkonia_massiliensis | 马赛涅斯捷连科菌 | 42/2642740 | 0.0016 | 1 | 1 | 1 | Nesterenkonia | 涅斯捷连科菌属 | 5 | 5 | 1 | 1 | 2 | 2 | G+ | 0.02 | 0.1 | 0.007 | 0.0299 | - | - | id¦15990152¦BAC¦R_6858122¦ | id¦46296864¦BAC¦S_3236868¦
source water 2 | Peptoniphilus_harei | 黑尔嗜胨菌 | 252/1739102 | 0.0145 | 1 | 6 | 5 | Peptoniphilus | 嗜胨菌属 | 8 | 5 | 2 | 2 | 3 | 2 | G+ | 0.22 | 0.29 | 0.0637 | 0.083 | 1 | 0.58 | id¦11863746¦BAC¦R_0349651¦ | id¦30360034¦BAC¦S_3835701¦
source water 2 | Peptoniphilus_grossensis | 肥胖嗜胨菌 | 42/2030597 | 0.0021 | 1 | 1 | 0 | Peptoniphilus | 嗜胨菌属 | 8 | 5 | 1 | 0 | 3 | 2 | G+ | 0.03 | 0.29 | 0.0091 | 0.083 | - | - | id¦70817098¦BAC¦R_2422848¦ | id¦52851796¦BAC¦S_8016240¦
source water 2 | Sphingobacterium_nematocida | 杀线虫鞘氨醇杆菌 | 84/5047352 | 0.0017 | 1 | 2 | 2 | Sphingobacterium | 鞘氨醇杆菌属 | 5 | 5 | 1 | 1 | 2 | 2 | G- | 0.03 | 0.07 | 0.0073 | 0.0196 | - | - | id¦18510945¦BAC¦R_6099857¦ | id¦44276539¦BAC¦S_8999429¦
source water 2 | Sphingobacterium_cavernae | 洞穴鞘氨醇杆菌 | 42/4054565 | 0.001 | 1 | 1 | 1 | Sphingobacterium | 鞘氨醇杆菌属 | 5 | 5 | 1 | 1 | 2 | 2 | G- | 0.02 | 0.07 | 0.0046 | 0.0196 | - | - | id¦00214940¦BAC¦R_1535601¦ | id¦10968391¦BAC¦S_1611697¦
source water 2 | Sphingobacterium_lactis | 乳鞘氨醇杆菌 | 42/4030188 | 0.001 | 1 | 1 | 1 | Sphingobacterium | 鞘氨醇杆菌属 | 5 | 5 | 1 | 1 | 2 | 2 | G- | 0.02 | 0.07 | 0.0046 | 0.0196 | - | - | id¦25930705¦BAC¦R_8138950¦ | id¦11271582¦BAC¦S_7600134¦
source water 2 | Sphingobacterium_multivorum | 多食鞘氨醇杆菌 | 42/6009687 | 0.0007 | 1 | 1 | 1 | Sphingobacterium | 鞘氨醇杆菌属 | 5 | 5 | 1 | 1 | 2 | 2 | G- | 0.01 | 0.07 | 0.0031 | 0.0196 | - | - | id¦21027335¦BAC¦R_4993630¦ | id¦04755840¦BAC¦S_5848964¦
source water 2 | Tepidimonas_fonticaldi | - | 163/3003536 | 0.0054 | 1 | 5 | 2 | Tepidimonas | - | 10 | 5 | 2 | 1 | 4 | 2 | G- | 0.11 | 0.22 | 0.0307 | 0.0649 | 1 | 0.63 | id¦36824863¦BAC¦R_2266445¦ | id¦23800547¦BAC¦S_5125954¦
source water 2 | Tepidimonas_charontis | - | 84/2791795 | 0.003 | 1 | 2 | 1 | Tepidimonas | - | 10 | 5 | 1 | 1 | 4 | 2 | G- | 0.05 | 0.22 | 0.0132 | 0.0649 | - | - | id¦29004486¦BAC¦R_4033284¦ | id¦15538534¦BAC¦S_6320333¦
source water 2 | Aeromonas_caviae | 豚鼠气单胞菌 | 126/4702913 | 0.0027 | 1 | 3 | 1 | Aeromonas | 气单胞菌属 | 8 | 4 | 1 | 1 | 3 | 1 | G- | 0.04 | 0.11 | 0.0118 | 0.0316 | - | - | id¦30017948¦BAC¦R_6892734¦ | id¦37818795¦BAC¦S_2582295¦
source water 2 | Aeromonas_enteropelogenes | 肠棕气单胞菌 | 42/4330051 | 0.001 | 1 | 1 | 0 | Aeromonas | 气单胞菌属 | 8 | 4 | 1 | 0 | 3 | 1 | G- | 0.01 | 0.11 | 0.0043 | 0.0316 | - | - | id¦21842765¦BAC¦R_4417081¦ | id¦27212229¦BAC¦S_8829888¦
source water 2 | Alkalibacterium_thalassium | 深海碱小杆菌 | 168/2360989 | 0.0071 | 1 | 4 | 3 | Alkalibacterium | 碱小杆菌属 | 5 | 4 | 1 | 1 | 2 | 1 | G+ | 0.11 | 0.13 | 0.0313 | 0.0383 | 1 | 0.95 | id¦30418402¦BAC¦R_3771578¦ | id¦92770326¦BAC¦S_4854572¦
source water 2 | Alkalibacterium_pelagium | 海洋碱小杆菌 | 42/2636818 | 0.0016 | 1 | 1 | 1 | Alkalibacterium | 碱小杆菌属 | 5 | 4 | 1 | 1 | 2 | 1 | G+ | 0.02 | 0.13 | 0.007 | 0.0383 | - | - | id¦05027244¦BAC¦R_7206892¦ | id¦62510368¦BAC¦S_8101017¦
source water 2 | Aquimonas_voraii | 沃氏水单胞菌 | 336/4428522 | 0.0076 | 1 | 8 | 4 | Aquimonas | 水单胞菌属 | 8 | 4 | 3 | 1 | 3 | 1 | G- | 0.11 | 0.11 | 0.0333 | 0.0333 | 1 | 0.95 | id¦47014223¦BAC¦R_6860881¦ | id¦45855135¦BAC¦S_7088958¦
source water 2 | Aureimonas_altamirensis | 阿尔塔米拉洞金色单胞菌 | 210/4190780 | 0.005 | 1 | 7 | 4 | Aureimonas | 金色单胞菌属 | 7 | 4 | 3 | 1 | 3 | 1 | G- | 0.11 | 0.11 | 0.0308 | 0.0308 | 1 | 0.61 | id¦51150278¦BAC¦R_1841800¦ | id¦88964670¦BAC¦S_8251232¦
source water 2 | Flavobacterium_endophyticum | 内生黄杆菌 | 42/3744919 | 0.0011 | 1 | 1 | 1 | Flavobacterium | 黄杆菌属 | 8 | 4 | 1 | 1 | 3 | 1 | G- | 0.02 | 0.15 | 0.0049 | 0.0426 | - | - | id¦30252850¦BAC¦R_2701441¦ | id¦19911554¦BAC¦S_0183230¦
source water 2 | Flavobacterium_lindanitolerans | 耐林丹黄杆菌 | 76/3722887 | 0.002 | 1 | 2 | 1 | Flavobacterium | 黄杆菌属 | 8 | 4 | 1 | 1 | 3 | 1 | G- | 0.03 | 0.15 | 0.0099 | 0.0426 | - | - | id¦85611026¦BAC¦R_3768758¦ | id¦54486492¦BAC¦S_1900512¦
source water 2 | Fusicatenibacter_saccharivorans | - | 126/3867499 | 0.0033 | 1 | 4 | 4 | Fusicatenibacter | - | 4 | 4 | 1 | 1 | 1 | 1 | G+ | 0.07 | 0.07 | 0.0191 | 0.0191 | - | - | id¦18562625¦BAC¦R_6984935¦ | id¦06149648¦BAC¦S_1363717¦
source water 2 | Gemella_sanguinis | 血孪生球菌 | 84/1795471 | 0.0047 | 1 | 3 | 3 | Gemella | 孪生球菌属 | 5 | 4 | 1 | 1 | 2 | 1 | G+ | 0.11 | 0.17 | 0.0308 | 0.0504 | - | - | id¦30794189¦BAC¦R_8718544¦ | id¦69707973¦BAC¦S_8295401¦
source water 2 | Gemella_haemolysans | 溶血孪生球菌 | 42/1881246 | 0.0022 | 1 | 2 | 1 | Gemella | 孪生球菌属 | 5 | 4 | 1 | 1 | 2 | 1 | G+ | 0.07 | 0.17 | 0.0196 | 0.0504 | - | - | id¦34286850¦BAC¦R_8980988¦ | id¦31233011¦BAC¦S_0664854¦
source water 2 | Haemophilus_parainfluenzae | 副流感嗜血杆菌 | 84/2126611 | 0.0039 | 1 | 6 | 3 | Haemophilus | 嗜血杆菌属 | 7 | 4 | 2 | 1 | 3 | 1 | G- | 0.18 | 0.21 | 0.0521 | 0.0609 | - | - | id¦16059935¦BAC¦R_6721919¦ | id¦77177367¦BAC¦S_3784721¦
source water 2 | Haemophilus_parahaemolyticus | 副溶血嗜血杆菌 | 42/2090133 | 0.002 | 1 | 1 | 1 | Haemophilus | 嗜血杆菌属 | 7 | 4 | 1 | 1 | 3 | 1 | G- | 0.03 | 0.21 | 0.0088 | 0.0609 | - | - | id¦73896511¦BAC¦R_4282757¦ | id¦00930571¦BAC¦S_6950772¦
source water 2 | Meiothermus_ruber | 红色亚栖热菌 | 84/3098791 | 0.0027 | 1 | 2 | 1 | Meiothermus | 亚栖热菌属 | 7 | 4 | 1 | 1 | 3 | 1 | G- | 0.04 | 0.15 | 0.0119 | 0.0435 | - | - | id¦77957809¦BAC¦R_6323764¦ | id¦53929864¦BAC¦S_7949413¦
source water 2 | Meiothermus_silvanus | 森林亚栖热菌 | 42/3249394 | 0.0013 | 1 | 1 | 1 | Meiothermus | 亚栖热菌属 | 7 | 4 | 1 | 1 | 3 | 1 | G- | 0.02 | 0.15 | 0.0057 | 0.0435 | - | - | id¦38072918¦BAC¦R_5433606¦ | id¦27760635¦BAC¦S_9719475¦
source water 2 | Methylorubrum_populi | - | 84/5705640 | 0.0015 | 1 | 4 | 2 | Methylorubrum | - | 7 | 4 | 1 | 1 | 3 | 1 | G- | 0.04 | 0.08 | 0.0129 | 0.0231 | - | - | id¦02926722¦BAC¦R_0191195¦ | id¦03193099¦BAC¦S_2396063¦
source water 2 | Methylorubrum_extorquens | - | 42/5511322 | 0.0008 | 1 | 2 | 0 | Methylorubrum | - | 7 | 4 | 1 | 0 | 3 | 1 | G- | 0.02 | 0.08 | 0.0067 | 0.0231 | - | - | id¦05740069¦BAC¦R_4313435¦ | id¦28594887¦BAC¦S_0183068¦
source water 2 | Morganella_morganii | 摩根摩根菌 | 84/4004672 | 0.0021 | 1 | 4 | 3 | Morganella | 摩根菌属 | 4 | 4 | 1 | 1 | 1 | 1 | G- | 0.06 | 0.06 | 0.0184 | 0.0184 | - | - | id¦02444203¦BAC¦R_0956223¦ | id¦04110010¦BAC¦S_0338628¦
source water 2 | Ornithinibacter_aureus | 金色鸟氨酸杆菌 | 248/3695644 | 0.0067 | 1 | 6 | 4 | Ornithinibacter | 鸟氨酸杆菌属 | 6 | 4 | 2 | 1 | 2 | 1 | G+ | 0.1 | 0.1 | 0.03 | 0.03 | 1 | 0.92 | id¦88286057¦BAC¦R_8403305¦ | id¦22697159¦BAC¦S_4277576¦
source water 2 | Pseudonocardia_ammonioxydans | 氨氧化假诺卡菌 | 42/7363171 | 0.0006 | 1 | 1 | 1 | Pseudonocardia | 假诺卡菌属 | 7 | 4 | 1 | 1 | 3 | 1 | G+ | 0.01 | 0.06 | 0.0025 | 0.0181 | - | - | id¦51073921¦BAC¦R_3106318¦ | id¦35795493¦BAC¦S_0101901¦
source water 2 | Pseudonocardia_alni | 桤木假诺卡菌 | 80/5994827 | 0.0013 | 1.05 | 2 | 0 | Pseudonocardia | 假诺卡菌属 | 7 | 4 | 1 | 0 | 3 | 1 | G+ | 0.02 | 0.06 | 0.0062 | 0.0181 | - | - | id¦59034585¦BAC¦R_1634020¦ | id¦60530659¦BAC¦S_7752583¦
source water 2 | Reyranella_massiliensis | - | 458/5771504 | 0.0079 | 1 | 11 | 4 | Reyranella | - | 11 | 4 | 4 | 1 | 4 | 1 | G- | 0.12 | 0.12 | 0.0352 | 0.0352 | 1 | 0.94 | id¦56998062¦BAC¦R_4249962¦ | id¦37825284¦BAC¦S_9192990¦
source water 2 | Rothia_mucilaginosa | 黏液罗氏菌 | 84/2253579 | 0.0037 | 1 | 6 | 3 | Rothia | 罗氏菌属 | 9 | 4 | 2 | 1 | 3 | 1 | G+ | 0.17 | 0.24 | 0.0491 | 0.0705 | - | - | id¦11637400¦BAC¦R_8187461¦ | id¦64873621¦BAC¦S_0860975¦
source water 2 | Rothia_dentocariosa | 龋齿罗氏菌 | 42/2415086 | 0.0017 | 1 | 1 | 1 | Rothia | 罗氏菌属 | 9 | 4 | 1 | 1 | 3 | 1 | G+ | 0.03 | 0.24 | 0.0076 | 0.0705 | - | - | id¦73897219¦BAC¦R_2444668¦ | id¦50670100¦BAC¦S_5532997¦
source water 2 | Rubellimicrobium_roseum | - | 285/4852361 | 0.0059 | 1 | 7 | 3 | Rubellimicrobium | - | 8 | 4 | 3 | 1 | 3 | 1 | G- | 0.09 | 0.1 | 0.0266 | 0.0303 | 1 | 0.62 | id¦31784287¦BAC¦R_2800080¦ | id¦26027014¦BAC¦S_0794312¦
source water 2 | Rubellimicrobium_mesophilum | - | 42/4920904 | 0.0009 | 1 | 1 | 0 | Rubellimicrobium | - | 8 | 4 | 1 | 0 | 3 | 1 | G- | 0.01 | 0.1 | 0.0037 | 0.0303 | - | - | id¦42298572¦BAC¦R_4684524¦ | id¦96258607¦BAC¦S_0970590¦
source water 2 | Stenotrophomonas_maltophilia | 嗜麦芽窄食单胞菌 | 210/4928653 | 0.0043 | 1 | 14 | 3 | Stenotrophomonas | 窄食单胞菌属 | 31 | 4 | 5 | 1 | 11 | 1 | G- | 0.18 | 0.44 | 0.0524 | 0.1281 | 1 | 0.96 | id¦55851721¦BAC¦R_2396079¦ | id¦75406125¦BAC¦S_6497236¦
source water 2 | Stenotrophomonas_acidaminiphila | 微嗜酸窄食单胞菌 | 120/3923927 | 0.0031 | 1 | 3 | 0 | Stenotrophomonas | 窄食单胞菌属 | 31 | 4 | 1 | 0 | 11 | 1 | G- | 0.05 | 0.44 | 0.0141 | 0.1281 | - | - | id¦67439370¦BAC¦R_0525270¦ | id¦90353891¦BAC¦S_8422845¦
source water 2 | Abiotrophia_defectiva | 缺陷乏养菌 | 126/2046826 | 0.0062 | 1 | 3 | 3 | Abiotrophia | 营养缺陷菌属 | 3 | 3 | 1 | 1 | 1 | 1 | G+ | 0.09 | 0.09 | 0.027 | 0.027 | - | - | id¦02848317¦BAC¦R_9947759¦ | id¦99770673¦BAC¦S_6049361¦
source water 2 | Aerococcus_viridans | 浅绿色气球菌 | 84/2003760 | 0.0042 | 1 | 2 | 2 | Aerococcus | 气球菌属 | 4 | 3 | 1 | 1 | 1 | 1 | G+ | 0.06 | 0.12 | 0.0184 | 0.035 | - | - | id¦86518983¦BAC¦R_3438489¦ | id¦48283804¦BAC¦S_8769117¦
source water 2 | Aerococcus_urinaeequi | 马脲气球菌 | 84/2223009 | 0.0038 | 1 | 2 | 0 | Aerococcus | 气球菌属 | 4 | 3 | 1 | 0 | 1 | 1 | G+ | 0.06 | 0.12 | 0.0166 | 0.035 | - | - | id¦26968257¦BAC¦R_7559823¦ | id¦08407767¦BAC¦S_0220225¦
source water 2 | Cellulomonas_marina | 海纤维单胞菌 | 122/3962952 | 0.0031 | 1 | 3 | 2 | Cellulomonas | 纤维单胞菌属 | 8 | 3 | 1 | 1 | 3 | 1 | G+ | 0.05 | 0.16 | 0.014 | 0.0468 | - | - | id¦89682971¦BAC¦R_8789578¦ | id¦94764568¦BAC¦S_7604189¦
source water 2 | Cellulomonas_fimi | 粪碱纤维单胞菌 | 42/4266344 | 0.001 | 1 | 1 | 0 | Cellulomonas | 纤维单胞菌属 | 8 | 3 | 1 | 0 | 3 | 1 | G+ | 0.01 | 0.16 | 0.0043 | 0.0468 | - | - | id¦98383000¦BAC¦R_3962416¦ | id¦93869191¦BAC¦S_6996394¦
source water 2 | Chitinimonas_taiwanensis | - | 159/4074938 | 0.0039 | 1.06 | 4 | 3 | Chitinimonas | - | 4 | 3 | 1 | 1 | 1 | 1 | G- | 0.06 | 0.06 | 0.0181 | 0.0181 | 0.95 | 0.95 | id¦64264746¦BAC¦R_2149456¦ | id¦10489068¦BAC¦S_4235107¦
source water 2 | Cupriavidus_metallidurans | 耐金属贪铜菌 | 84/6800126 | 0.0012 | 1 | 2 | 2 | Cupriavidus | 贪铜菌属 | 11 | 3 | 1 | 1 | 4 | 1 | G- | 0.02 | 0.11 | 0.0054 | 0.0309 | - | - | id¦00480215¦BAC¦R_5315201¦ | id¦62466261¦BAC¦S_1224361¦
source water 2 | Cupriavidus_gilardii | 吉拉迪贪铜菌 | 42/4874600 | 0.0009 | 1 | 2 | 1 | Cupriavidus | 贪铜菌属 | 11 | 3 | 1 | 1 | 4 | 1 | G- | 0.03 | 0.11 | 0.0076 | 0.0309 | - | - | id¦20893179¦BAC¦R_0594976¦ | id¦74989045¦BAC¦S_8863800¦
source water 2 | Fusobacterium_nucleatum | 具核梭杆菌 | 84/2261267 | 0.0037 | 1 | 3 | 0 | Fusobacterium | 梭杆菌属 | 3 | 3 | 1 | 0 | 1 | 1 | G- | 0.08 | 0.08 | 0.0245 | 0.0245 | - | - | id¦81591667¦BAC¦R_2873009¦ | id¦77964578¦BAC¦S_3772641¦
source water 2 | Geobacillus_thermoleovorans | 高温烷烃地芽胞杆菌 | 206/3354224 | 0.0061 | 1 | 5 | 1 | Geobacillus | 地芽胞杆菌属 | 8 | 3 | 2 | 1 | 3 | 1 | G+ | 0.09 | 0.15 | 0.0275 | 0.0436 | 1 | 0.46 | id¦66240092¦BAC¦R_1833063¦ | id¦89511491¦BAC¦S_9182282¦
source water 2 | [Bacillus]_caldolyticus | 热溶芽胞杆菌 | 37/3457580 | 0.0011 | 1 | 1 | 0 | Geobacillus | 地芽胞杆菌属 | 8 | 3 | 1 | 0 | 3 | 1 | G+ | 0.02 | 0.15 | 0.0053 | 0.0436 | - | - | id¦20607314¦BAC¦R_3378635¦ | id¦07772093¦BAC¦S_8924878¦
source water 2 | Geodermatophilus_nigrescens | 变黑地嗜皮菌 | 42/4740574 | 0.0009 | 1 | 1 | 1 | Geodermatophilus | 地嗜皮菌属 | 10 | 3 | 1 | 1 | 4 | 1 | G+ | 0.01 | 0.12 | 0.0039 | 0.036 | - | - | id¦18927667¦BAC¦R_7816213¦ | id¦05034415¦BAC¦S_0769077¦
source water 2 | Geodermatophilus_amargosae | 阿马戈萨地嗜皮菌 | 42/5868899 | 0.0007 | 1 | 1 | 0 | Geodermatophilus | 地嗜皮菌属 | 10 | 3 | 1 | 0 | 4 | 1 | G+ | 0.01 | 0.12 | 0.0031 | 0.036 | - | - | id¦51353689¦BAC¦R_0710118¦ | id¦21336997¦BAC¦S_2155658¦
source water 2 | Gordonia_jacobaea | 戈登菌* | 84/4920736 | 0.0017 | 1 | 2 | 1 | Gordonia | 戈登菌属 | 6 | 3 | 1 | 1 | 2 | 1 | G+ | 0.03 | 0.08 | 0.0075 | 0.0227 | - | - | id¦26583045¦BAC¦R_2761421¦ | id¦60344843¦BAC¦S_1679961¦
source water 2 | Gordonia_westfalica | 威斯特菲尼亚戈登菌 | 42/6405373 | 0.0007 | 1 | 1 | 1 | Gordonia | 戈登菌属 | 6 | 3 | 1 | 1 | 2 | 1 | G+ | 0.01 | 0.08 | 0.0029 | 0.0227 | - | - | id¦13608522¦BAC¦R_2075707¦ | id¦59434172¦BAC¦S_1629223¦
source water 2 | Herbaspirillum_aquaticum | 水草螺菌 | 162/5419279 | 0.003 | 1 | 4 | 0 | Herbaspirillum | 草螺菌属 | 6 | 3 | 1 | 0 | 2 | 1 | G- | 0.05 | 0.07 | 0.0136 | 0.02 | 1 | 0.51 | id¦88547614¦BAC¦R_6001968¦ | id¦08418190¦BAC¦S_1750158¦
source water 2 | Herbaspirillum_huttiense | 赫氏草螺菌 | 84/5776621 | 0.0015 | 1 | 2 | 0 | Herbaspirillum | 草螺菌属 | 6 | 3 | 1 | 0 | 2 | 1 | G- | 0.02 | 0.07 | 0.0064 | 0.02 | - | - | id¦98608476¦BAC¦R_5564892¦ | id¦70324933¦BAC¦S_2440914¦
source water 2 | Leptotrichia_wadei | 韦德纤毛菌 | 126/2335974 | 0.0054 | 1 | 3 | 2 | Leptotrichia | 纤毛菌属 | 3 | 3 | 1 | 1 | 1 | 1 | G- | 0.08 | 0.08 | 0.0237 | 0.0237 | - | - | id¦05907475¦BAC¦R_3583748¦ | id¦24310541¦BAC¦S_5691087¦
source water 2 | Lysobacter_enzymogenes | 产酶溶杆菌 | 120/6330575 | 0.0019 | 1 | 5 | 1 | Lysobacter | 溶杆菌属 | 40 | 3 | 2 | 1 | 15 | 1 | G- | 0.05 | 0.69 | 0.0146 | 0.2001 | - | - | id¦33179919¦BAC¦R_3684177¦ | id¦72169287¦BAC¦S_7483574¦
source water 2 | Lysobacter_alkalisoli | 碱土溶杆菌 | 42/3857091 | 0.0011 | 1 | 1 | 0 | Lysobacter | 溶杆菌属 | 40 | 3 | 1 | 0 | 15 | 1 | G- | 0.02 | 0.69 | 0.0048 | 0.2001 | - | - | id¦67929811¦BAC¦R_5072478¦ | id¦49031704¦BAC¦S_0615917¦
source water 2 | Myxococcus_fulvus | 橙色粘球菌 | 210/10824089 | 0.0019 | 1 | 5 | 3 | Myxococcus | 粘球菌属 | 7 | 3 | 2 | 1 | 3 | 1 | G- | 0.03 | 0.04 | 0.0085 | 0.0125 | 1 | 0.61 | id¦85226113¦BAC¦R_3145394¦ | id¦77991068¦BAC¦S_7478282¦
source water 2 | Myxococcus_xanthus | 黄色粘球菌 | 42/9139763 | 0.0005 | 1 | 2 | 0 | Myxococcus | 粘球菌属 | 7 | 3 | 1 | 0 | 3 | 1 | G- | 0.01 | 0.04 | 0.004 | 0.0125 | - | - | id¦36793586¦BAC¦R_1855433¦ | id¦30021974¦BAC¦S_6022232¦
source water 2 | Pararheinheimera_texasensis | - | 123/4585314 | 0.0027 | 1 | 3 | 3 | Pararheinheimera | - | 3 | 3 | 1 | 1 | 1 | 1 | G- | 0.04 | 0.04 | 0.0121 | 0.0121 | - | - | id¦67475083¦BAC¦R_9987499¦ | id¦70413396¦BAC¦S_7696476¦
source water 2 | Porphyromonas_somerae | 索氏卟啉单胞菌 | 155/2331888 | 0.0066 | 1.05 | 4 | 3 | Porphyromonas | 卟啉单胞菌属 | 4 | 3 | 1 | 1 | 1 | 1 | G- | 0.11 | 0.11 | 0.0317 | 0.0317 | 0.95 | 0.95 | id¦96851740¦BAC¦R_0204517¦ | id¦47795490¦BAC¦S_6105005¦
source water 2 | Roseateles_aquatilis | 水生玫瑰色半光合菌 | 126/6381253 | 0.002 | 1 | 3 | 3 | Roseateles | 玫瑰色半光合菌属 | 4 | 3 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.04 | 0.0087 | 0.012 | - | - | id¦40767666¦BAC¦R_7003072¦ | id¦11108759¦BAC¦S_1190084¦
source water 2 | Roseateles_terrae | 土壤玫瑰色半光合菌 | 42/5518057 | 0.0008 | 1 | 1 | 0 | Roseateles | 玫瑰色半光合菌属 | 4 | 3 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.04 | 0.0033 | 0.012 | - | - | id¦66992261¦BAC¦R_5589020¦ | id¦34631173¦BAC¦S_9804374¦
source water 2 | Roseomonas_mucosa | 黏液玫瑰单胞菌 | 84/4966677 | 0.0017 | 1 | 2 | 1 | Roseomonas | 玫瑰单胞菌属 | 5 | 3 | 1 | 1 | 2 | 1 | G- | 0.03 | 0.06 | 0.0074 | 0.0177 | - | - | id¦62049470¦BAC¦R_4773523¦ | id¦87523695¦BAC¦S_6220312¦
source water 2 | Roseomonas_deserti | 沙漠玫瑰单胞菌 | 42/5284190 | 0.0008 | 1 | 1 | 0 | Roseomonas | 玫瑰单胞菌属 | 5 | 3 | 1 | 0 | 2 | 1 | G- | 0.01 | 0.06 | 0.0035 | 0.0177 | - | - | id¦23893468¦BAC¦R_4132273¦ | id¦99227615¦BAC¦S_0491908¦
source water 2 | Skermanella_aerolata | - | 126/8501121 | 0.0015 | 1 | 3 | 3 | Skermanella | - | 5 | 3 | 1 | 1 | 2 | 1 | G- | 0.02 | 0.04 | 0.0065 | 0.012 | - | - | id¦55639058¦BAC¦R_7772353¦ | id¦85538285¦BAC¦S_1961797¦
source water 2 | Skermanella_pratensis | - | 42/5869433 | 0.0007 | 1 | 1 | 0 | Skermanella | - | 5 | 3 | 1 | 0 | 2 | 1 | G- | 0.01 | 0.04 | 0.0031 | 0.012 | - | - | id¦34839885¦BAC¦R_6516635¦ | id¦66653991¦BAC¦S_6265323¦
source water 2 | Streptomyces_thermoautotrophicus | 热自养链霉菌 | 42/5134336 | 0.0008 | 1 | 1 | 1 | Streptomyces | 链霉菌属 | 12 | 3 | 1 | 1 | 4 | 1 | G+ | 0.01 | 0.1 | 0.0036 | 0.0282 | - | - | id¦45774606¦BAC¦R_0478964¦ | id¦95140353¦BAC¦S_9709909¦
source water 2 | [Kitasatospora]_papulosa | 丘疹北里孢菌 | 42/7553841 | 0.0006 | 1 | 1 | 0 | Streptomyces | 链霉菌属 | 12 | 3 | 1 | 0 | 4 | 1 | G+ | 0.01 | 0.1 | 0.0024 | 0.0282 | - | - | id¦61082008¦BAC¦R_1193301¦ | id¦97579528¦BAC¦S_1311618¦
source water 2 | Sulfurihydrogenibium_azorense | - | 167/1640877 | 0.0102 | 1.26 | 5 | 3 | Sulfurihydrogenibium | - | 5 | 3 | 2 | 1 | 2 | 1 | G- | 0.19 | 0.19 | 0.0562 | 0.0562 | 0.8 | 0 | id¦26688492¦BAC¦R_0063670¦ | id¦59989486¦BAC¦S_7162527¦
source water 2 | Tessaracoccus_bendigoensis | 本迪戈四合球菌 | 42/4132567 | 0.001 | 1 | 1 | 1 | Tessaracoccus | 四合球菌属 | 4 | 3 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.08 | 0.0045 | 0.0218 | - | - | id¦40285537¦BAC¦R_0225571¦ | id¦94704965¦BAC¦S_6397940¦
source water 2 | Tessaracoccus_flavus | 黄色四合球菌 | 42/3222890 | 0.0013 | 1 | 1 | 1 | Tessaracoccus | 四合球菌属 | 4 | 3 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.08 | 0.0057 | 0.0218 | - | - | id¦48626808¦BAC¦R_8495080¦ | id¦82619272¦BAC¦S_7349508¦
source water 2 | Thermoanaerobacter_brockii | 布洛克热厌氧杆菌 | 42/2344824 | 0.0018 | 1 | 1 | 0 | Thermoanaerobacter | 热厌氧杆菌属 | 7 | 3 | 1 | 0 | 3 | 1 | G+ | 0.03 | 0.18 | 0.0079 | 0.0532 | - | - | id¦84293320¦BAC¦R_3180678¦ | id¦36576488¦BAC¦S_1179888¦
source water 2 | Thermoanaerobacter_ethanolicus | 乙醇热厌氧杆菌 | 78/2911280 | 0.0027 | 1 | 2 | 0 | Thermoanaerobacter | 热厌氧杆菌属 | 7 | 3 | 1 | 0 | 3 | 1 | Gram-variable | 0.04 | 0.18 | 0.0127 | 0.0532 | - | - | id¦53966050¦BAC¦R_4544884¦ | id¦16986635¦BAC¦S_7704850¦
source water 2 | Xanthomonas_campestris | 野油菜黄单胞菌 | 42/5052842 | 0.0008 | 1 | 2 | 2 | Xanthomonas | 黄单胞菌属 | 22 | 3 | 1 | 1 | 8 | 1 | G- | 0.03 | 0.29 | 0.0073 | 0.0843 | - | - | id¦19845644¦BAC¦R_9909875¦ | id¦72428435¦BAC¦S_8827926¦
source water 2 | Xanthomonas_alfalfae | 苜蓿黄单胞菌 | 42/4892941 | 0.0009 | 1 | 1 | 0 | Xanthomonas | 黄单胞菌属 | 22 | 3 | 1 | 0 | 8 | 1 | G- | 0.01 | 0.29 | 0.0038 | 0.0843 | - | - | id¦05870435¦BAC¦R_2168608¦ | id¦88596221¦BAC¦S_6068664¦
source water 2 | Aggregatibacter_segnis | 惰性凝聚杆菌 | 42/2002456 | 0.0021 | 1 | 2 | 2 | Aggregatibacter | 凝聚杆菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G- | 0.06 | 0.06 | 0.0184 | 0.0184 | - | - | id¦64069159¦BAC¦R_9027896¦ | id¦28162889¦BAC¦S_4466289¦
source water 2 | Alishewanella_aestuarii | 潮汐别样希瓦菌 | 84/3586920 | 0.0023 | 1 | 2 | 1 | Alishewanella | 别样希瓦菌属 | 5 | 2 | 1 | 1 | 2 | 1 | G- | 0.04 | 0.09 | 0.0103 | 0.0247 | - | - | id¦27886809¦BAC¦R_9627872¦ | id¦74468001¦BAC¦S_9428413¦
source water 2 | Alishewanella_jeotgali | 发酵海鲜别样希瓦菌 | 117/3831997 | 0.0031 | 1 | 3 | 1 | Alishewanella | 别样希瓦菌属 | 5 | 2 | 1 | 1 | 2 | 1 | G- | 0.05 | 0.09 | 0.0144 | 0.0247 | - | - | id¦95256735¦BAC¦R_6865440¦ | id¦28910703¦BAC¦S_7528962¦
source water 2 | Aminobacter_aminovorans | 嗜氨基氨基杆菌 | 122/5623946 | 0.0022 | 1 | 3 | 2 | Aminobacter | 氨基杆菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.03 | 0.0098 | 0.0098 | - | - | id¦58477872¦BAC¦R_9616693¦ | id¦91757388¦BAC¦S_3020805¦
source water 2 | Atopobium_parvulum | 极小陌生菌 | 42/1527399 | 0.0027 | 1 | 1 | 1 | Atopobium | 陌生菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G+ | 0.04 | 0.09 | 0.0121 | 0.025 | - | - | id¦30051589¦BAC¦R_2978760¦ | id¦23054861¦BAC¦S_8819107¦
source water 2 | Atopobium_vaginae | 阴道陌生菌 | 42/1430105 | 0.0029 | 1 | 1 | 1 | Atopobium | 陌生菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G+ | 0.04 | 0.09 | 0.0129 | 0.025 | - | - | id¦45102282¦BAC¦R_4631490¦ | id¦07894984¦BAC¦S_4366575¦
source water 2 | Azospira_oryzae | 水稻固氮螺菌 | 120/3450497 | 0.0035 | 1 | 3 | 2 | Azospira | 固氮螺菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G- | 0.06 | 0.06 | 0.016 | 0.016 | - | - | id¦53610670¦BAC¦R_3944454¦ | id¦83599120¦BAC¦S_8323483¦
source water 2 | Bordetella_ansorpii | 鲍特菌* | 84/6147526 | 0.0014 | 1 | 2 | 2 | Bordetella | 鲍特菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.03 | 0.006 | 0.0097 | - | - | id¦38069916¦BAC¦R_7721742¦ | id¦01185738¦BAC¦S_4565564¦
source water 2 | Bordetella_petrii | 派替咳鲍特菌 | 42/5043660 | 0.0008 | 1 | 1 | 0 | Bordetella | 鲍特菌属 | 3 | 2 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.03 | 0.0037 | 0.0097 | - | - | id¦32420686¦BAC¦R_3792745¦ | id¦59644894¦BAC¦S_9877587¦
source water 2 | Capnocytophaga_gingivalis | 牙龈二氧化碳噬纤维菌 | 42/2838633 | 0.0015 | 1 | 1 | 1 | Capnocytophaga | 二氧化碳噬纤维菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.05 | 0.0065 | 0.0139 | - | - | id¦93171430¦BAC¦R_6500067¦ | id¦31765661¦BAC¦S_2463671¦
source water 2 | Capnocytophaga_leadbetteri | 利氏二氧化碳噬纤维菌 | 42/2504023 | 0.0017 | 1 | 1 | 1 | Capnocytophaga | 二氧化碳噬纤维菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.05 | 0.0074 | 0.0139 | - | - | id¦03706728¦BAC¦R_2601016¦ | id¦03490795¦BAC¦S_2272509¦
source water 2 | Cytophaga_aurantiaca | 橙黄噬纤维菌 | 210/4423005 | 0.0047 | 1 | 5 | 1 | Cytophaga | 噬纤维菌属 | 6 | 2 | 2 | 1 | 2 | 1 | G- | 0.07 | 0.09 | 0.0209 | 0.0251 | 1 | 0.96 | id¦64974078¦BAC¦R_5321670¦ | id¦58943146¦BAC¦S_8637269¦
source water 2 | Cytophaga_hutchinsonii | 哈氏噬纤维菌 | 42/4433218 | 0.0009 | 1 | 1 | 0 | Cytophaga | 噬纤维菌属 | 6 | 2 | 1 | 0 | 2 | 1 | G- | 0.01 | 0.09 | 0.0042 | 0.0251 | - | - | id¦01904224¦BAC¦R_7208223¦ | id¦10417686¦BAC¦S_9669581¦
source water 2 | Dietzia_natronolimnaea | 碱湖迪茨菌 | 42/3768419 | 0.0011 | 1 | 1 | 1 | Dietzia | 迪茨菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.05 | 0.0049 | 0.0151 | - | - | id¦50109664¦BAC¦R_7422836¦ | id¦45812697¦BAC¦S_8733499¦
source water 2 | Dietzia_timorensis | 帝汶迪茨菌 | 42/3607892 | 0.0012 | 1 | 1 | 1 | Dietzia | 迪茨菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.05 | 0.0051 | 0.0151 | - | - | id¦08555213¦BAC¦R_3886335¦ | id¦18431671¦BAC¦S_6575051¦
source water 2 | Fenollaria_timonensis | - | 84/1738886 | 0.0048 | 1 | 2 | 1 | Fenollaria | - | 2 | 2 | 1 | 1 | 1 | 1 | G- | 0.07 | 0.07 | 0.0212 | 0.0212 | - | - | id¦24454262¦BAC¦R_6254730¦ | id¦81213742¦BAC¦S_0262130¦
source water 2 | Gardnerella_vaginalis | 阴道加德纳菌 | 84/1743222 | 0.0048 | 1 | 2 | 2 | Gardnerella | 加德纳菌属 | 2 | 2 | 1 | 1 | 1 | 1 | Gram-variable | 0.07 | 0.07 | 0.0212 | 0.0212 | - | - | id¦08433451¦BAC¦R_9466552¦ | id¦24493786¦BAC¦S_3798852¦
source water 2 | Gemmobacter_caeni | 淤泥芽殖杆菌 | 450/5221099 | 0.0086 | 1 | 11 | 2 | Gemmobacter | 芽殖杆菌属 | 18 | 2 | 4 | 1 | 7 | 1 | G- | 0.13 | 0.24 | 0.0389 | 0.0694 | 1 | 0.97 | id¦41117377¦BAC¦R_1216033¦ | id¦73682540¦BAC¦S_7568825¦
source water 2 | Gemmobacter_aquaticus | 水生芽殖杆菌 | 42/3987105 | 0.0011 | 1 | 1 | 0 | Gemmobacter | 芽殖杆菌属 | 18 | 2 | 1 | 0 | 7 | 1 | G- | 0.02 | 0.24 | 0.0046 | 0.0694 | - | - | id¦05685949¦BAC¦R_4022124¦ | id¦30753983¦BAC¦S_9773668¦
source water 2 | Granulicatella_adiacens | 毗邻颗粒链菌 | 84/1923388 | 0.0044 | 1 | 2 | 2 | Granulicatella | 颗粒链菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G+ | 0.07 | 0.07 | 0.0192 | 0.0192 | - | - | id¦14208282¦BAC¦R_8828940¦ | id¦63289353¦BAC¦S_6129138¦
source water 2 | Ideonella_sakaiensis | - | 202/6100060 | 0.0033 | 1 | 5 | 2 | Ideonella | - | 5 | 2 | 2 | 1 | 2 | 1 | G- | 0.05 | 0.05 | 0.0151 | 0.0151 | 1 | 0.86 | id¦69820320¦BAC¦R_2024724¦ | id¦05437593¦BAC¦S_4927900¦
source water 2 | Intestinimonas_butyriciproducens | - | 84/3376475 | 0.0025 | 1 | 2 | 2 | Intestinimonas | - | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.04 | 0.05 | 0.0109 | 0.0158 | - | - | id¦51173191¦BAC¦R_5958134¦ | id¦05302643¦BAC¦S_3855469¦
source water 2 | Intestinimonas_massiliensis | - | 42/3754751 | 0.0011 | 1 | 1 | 0 | Intestinimonas | - | 3 | 2 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.05 | 0.0049 | 0.0158 | - | - | id¦25431188¦BAC¦R_4885835¦ | id¦19139837¦BAC¦S_0081143¦
source water 2 | Janthinobacterium_lividum | 蓝黑紫色杆菌 | 122/6399352 | 0.0019 | 1 | 3 | 1 | Janthinobacterium | 紫色杆菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.03 | 0.0087 | 0.0087 | - | - | id¦70033137¦BAC¦R_9469174¦ | id¦43411292¦BAC¦S_9137615¦
source water 2 | Kushneria_phyllosphaerae | 叶面库什纳菌 | 42/3743748 | 0.0011 | 1 | 1 | 1 | Kushneria | 库什纳菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.03 | 0.0049 | 0.0099 | - | - | id¦77179134¦BAC¦R_7745405¦ | id¦11923961¦BAC¦S_3013501¦
source water 2 | Kushneria_marisflavi | 黄海库什纳菌 | 42/3667185 | 0.0011 | 1 | 1 | 0 | Kushneria | 库什纳菌属 | 2 | 2 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.03 | 0.005 | 0.0099 | - | - | id¦01179416¦BAC¦R_1199985¦ | id¦35214669¦BAC¦S_4636328¦
source water 2 | Lautropia_mirabilis | 奇异劳特罗普菌 | 126/3172010 | 0.004 | 1 | 3 | 2 | Lautropia | 劳特罗普菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G- | 0.06 | 0.06 | 0.0175 | 0.0175 | - | - | id¦50555833¦BAC¦R_3773357¦ | id¦48261277¦BAC¦S_8489393¦
source water 2 | Marmoricola_aequoreus | - | 74/4158271 | 0.0018 | 1.14 | 2 | 1 | Marmoricola | - | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.03 | 0.05 | 0.0089 | 0.0134 | - | - | id¦07499779¦BAC¦R_9730893¦ | id¦53099320¦BAC¦S_9754533¦
source water 2 | Marmoricola_scoriae | - | 42/4058492 | 0.001 | 1 | 1 | 0 | Marmoricola | - | 3 | 2 | 1 | 0 | 1 | 1 | G+ | 0.02 | 0.05 | 0.0045 | 0.0134 | - | - | id¦39963273¦BAC¦R_5188263¦ | id¦28492378¦BAC¦S_8959617¦
source water 2 | Micavibrio_aeruginosavorus | 云母弧菌* | 84/2481983 | 0.0034 | 1 | 2 | 2 | Micavibrio | 云母弧菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G- | 0.05 | 0.05 | 0.0149 | 0.0149 | - | - | id¦88595630¦BAC¦R_5064219¦ | id¦53863284¦BAC¦S_0123829¦
source water 2 | Mycobacterium_lentiflavum | 慢生黄分枝杆菌 | 42/6817539 | 0.0006 | 1 | 1 | 1 | Mycobacterium | 分枝杆菌属 | 6 | 2 | 1 | 1 | 2 | 1 | G+ | 0.01 | 0.06 | 0.0027 | 0.0177 | - | - | id¦26132448¦BAC¦R_0601973¦ | id¦22286299¦BAC¦S_7407264¦
source water 2 | Mycobacterium_gordonae | 戈登分枝杆菌 | 42/6872267 | 0.0006 | 1 | 1 | 0 | Mycobacterium | 分枝杆菌属 | 6 | 2 | 1 | 0 | 2 | 1 | G+ | 0.01 | 0.06 | 0.0027 | 0.0177 | - | - | id¦07715604¦BAC¦R_2595268¦ | id¦38080696¦BAC¦S_6244383¦
source water 2 | Nakamurella_multipartita | 多瓣中村菌 | 42/6060298 | 0.0007 | 1 | 1 | 1 | Nakamurella | 中村菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.01 | 0.03 | 0.003 | 0.0096 | - | - | id¦68833772¦BAC¦R_5116181¦ | id¦33516989¦BAC¦S_1314463¦
source water 2 | Nakamurella_silvestris | 森林中村菌 | 42/5413321 | 0.0008 | 1 | 1 | 1 | Nakamurella | 中村菌属 | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.01 | 0.03 | 0.0034 | 0.0096 | - | - | id¦70112303¦BAC¦R_5764591¦ | id¦48192074¦BAC¦S_7755220¦
source water 2 | Neomicrococcus_aestuarii | - | 126/2667837 | 0.0047 | 1 | 3 | 2 | Neomicrococcus | - | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.07 | 0.07 | 0.0208 | 0.0208 | - | - | id¦14441373¦BAC¦R_6899757¦ | id¦13664816¦BAC¦S_4479204¦
source water 2 | Nocardia_testacea | 砖色诺卡菌 | 42/7255696 | 0.0006 | 1 | 1 | 1 | Nocardia | 诺卡菌属 | 5 | 2 | 1 | 1 | 2 | 1 | G+ | 0.01 | 0.04 | 0.0025 | 0.0126 | - | - | id¦80671870¦BAC¦R_2360603¦ | id¦26038697¦BAC¦S_2919589¦
source water 2 | Nocardia_vermiculata | 蠕虫诺卡菌 | 42/6702917 | 0.0006 | 1 | 1 | 1 | Nocardia | 诺卡菌属 | 5 | 2 | 1 | 1 | 2 | 1 | G+ | 0.01 | 0.04 | 0.0028 | 0.0126 | - | - | id¦33882215¦BAC¦R_7787059¦ | id¦47482119¦BAC¦S_9780793¦
source water 2 | Pantoea_brenneri | 布氏泛菌 | 42/5030352 | 0.0008 | 1 | 1 | 1 | Pantoea | 泛菌属 | 5 | 2 | 1 | 1 | 2 | 1 | G- | 0.01 | 0.06 | 0.0037 | 0.0186 | - | - | id¦89516993¦BAC¦R_7615405¦ | id¦59628336¦BAC¦S_7151034¦
source water 2 | Pantoea_agglomerans | 成团泛菌 | 77/5046542 | 0.0015 | 1 | 2 | 0 | Pantoea | 泛菌属 | 5 | 2 | 1 | 0 | 2 | 1 | G- | 0.03 | 0.06 | 0.0073 | 0.0186 | - | - | id¦18560918¦BAC¦R_8835157¦ | id¦07111782¦BAC¦S_3106872¦
source water 2 | Pelomonas_puraquae | - | 126/6056926 | 0.0021 | 1 | 3 | 2 | Pelomonas | - | 7 | 2 | 1 | 1 | 3 | 1 | G- | 0.03 | 0.08 | 0.0091 | 0.0219 | - | - | id¦47005438¦BAC¦R_6576497¦ | id¦00827443¦BAC¦S_8432294¦
source water 2 | Pelomonas_saccharophila | - | 168/5772002 | 0.0029 | 1 | 4 | 0 | Pelomonas | - | 7 | 2 | 1 | 0 | 3 | 1 | G- | 0.04 | 0.08 | 0.0128 | 0.0219 | 1 | 0.63 | id¦03744203¦BAC¦R_2298695¦ | id¦97409254¦BAC¦S_2675104¦
source water 2 | Piscicoccus_intestinalis | - | 84/4692305 | 0.0018 | 1 | 2 | 2 | Piscicoccus | - | 2 | 2 | 1 | 1 | 1 | 1 | G+ | 0.03 | 0.03 | 0.0079 | 0.0079 | - | - | id¦13145908¦BAC¦R_1415332¦ | id¦02863152¦BAC¦S_2597416¦
source water 2 | Sediminibacterium_salmoneum | 鲑色沉积物杆菌 | 84/3190244 | 0.0026 | 1 | 2 | 2 | Sediminibacterium | 沉积物杆菌属 | 2 | 2 | 1 | 1 | 1 | 1 | G- | 0.04 | 0.04 | 0.0116 | 0.0116 | - | - | id¦59889118¦BAC¦R_5717741¦ | id¦99070354¦BAC¦S_5731917¦
source water 2 | Shewanella_bicestrii | 希瓦菌* | 42/4800597 | 0.0009 | 1 | 1 | 0 | Shewanella | 希瓦菌属 | 4 | 2 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.05 | 0.0038 | 0.0149 | - | - | id¦74291313¦BAC¦R_0469147¦ | id¦44004178¦BAC¦S_2210488¦
source water 2 | Shewanella_canadensis | 加拿大希瓦菌 | 42/5677505 | 0.0007 | 1 | 1 | 0 | Shewanella | 希瓦菌属 | 4 | 2 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.05 | 0.0033 | 0.0149 | - | - | id¦09392415¦BAC¦R_4945852¦ | id¦48011855¦BAC¦S_5167561¦
source water 2 | Tetrasphaera_australiensis | - | 42/4217543 | 0.001 | 1 | 1 | 1 | Tetrasphaera | - | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.05 | 0.0044 | 0.0146 | - | - | id¦81335685¦BAC¦R_6920885¦ | id¦05103014¦BAC¦S_8533192¦
source water 2 | Tetrasphaera_jenkinsii | - | 42/3790726 | 0.0011 | 1 | 1 | 1 | Tetrasphaera | - | 3 | 2 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.05 | 0.0049 | 0.0146 | - | - | id¦23004623¦BAC¦R_3747733¦ | id¦92310114¦BAC¦S_2652751¦
source water 2 | Thauera_aminoaromatica | 芳香氨基酸索氏菌 | 84/4273109 | 0.002 | 1 | 3 | 0 | Thauera | 索氏菌属 | 8 | 2 | 1 | 0 | 3 | 1 | G- | 0.04 | 0.12 | 0.013 | 0.0348 | - | - | id¦83024249¦BAC¦R_6764794¦ | id¦95065729¦BAC¦S_7431496¦
source water 2 | Thauera_butanivorans | 食丁烷索氏菌 | 42/4793369 | 0.0009 | 1 | 1 | 0 | Thauera | 索氏菌属 | 8 | 2 | 1 | 0 | 3 | 1 | G- | 0.01 | 0.12 | 0.0038 | 0.0348 | - | - | id¦55978573¦BAC¦R_5532982¦ | id¦04173534¦BAC¦S_4776648¦
source water 2 | Agrobacterium_albertimagni | 土壤杆菌* | 42/5077547 | 0.0008 | 1 | 1 | 0 | Agrobacterium | 土壤杆菌属 | 6 | 1 | 1 | 0 | 2 | 1 | G- | 0.01 | 0.07 | 0.0036 | 0.0199 | - | - | id¦56411819¦BAC¦R_0882699¦ | id¦52391253¦BAC¦S_3707054¦
source water 2 | Agrobacterium_fabrum | 土壤杆菌* | 42/5685466 | 0.0007 | 1 | 1 | 0 | Agrobacterium | 土壤杆菌属 | 6 | 1 | 1 | 0 | 2 | 1 | G- | 0.01 | 0.07 | 0.0032 | 0.0199 | - | - | id¦35822614¦BAC¦R_1180413¦ | id¦28339672¦BAC¦S_0405156¦
source water 2 | Agrococcus_jenensis | 耶纳农球菌 | 42/2962035 | 0.0014 | 1 | 1 | 0 | Agrococcus | 农球菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0062 | 0.0062 | - | - | id¦68382912¦BAC¦R_9351835¦ | id¦03767084¦BAC¦S_4753346¦
source water 2 | Ancylobacter_aquaticus | 水生屈曲杆菌 | 42/4832089 | 0.0009 | 1 | 1 | 0 | Ancylobacter | 屈曲杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.03 | 0.0038 | 0.0079 | - | - | id¦07391713¦BAC¦R_8851887¦ | id¦88055554¦BAC¦S_5336022¦
source water 2 | Ancylobacter_rudongensis | 如东屈曲杆菌 | 42/4505254 | 0.0009 | 1 | 1 | 0 | Ancylobacter | 屈曲杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.03 | 0.0041 | 0.0079 | - | - | id¦65992456¦BAC¦R_5222823¦ | id¦65001160¦BAC¦S_9882652¦
source water 2 | Anoxybacillus_flavithermus | 好热黄厌氧芽胞杆菌 | 84/2636945 | 0.0032 | 1 | 2 | 1 | Anoxybacillus | 厌氧芽胞杆菌属 | 5 | 1 | 1 | 1 | 2 | 1 | G+ | 0.05 | 0.11 | 0.014 | 0.0331 | - | - | id¦20086135¦BAC¦R_1420673¦ | id¦44678430¦BAC¦S_7432090¦
source water 2 | Anoxybacillus_gonensis | 格嫩泉厌氧芽胞杆菌 | 37/2591418 | 0.0014 | 1 | 1 | 0 | Anoxybacillus | 厌氧芽胞杆菌属 | 5 | 1 | 1 | 0 | 2 | 1 | G+ | 0.02 | 0.11 | 0.0071 | 0.0331 | - | - | id¦11934261¦BAC¦R_4266892¦ | id¦58108189¦BAC¦S_5740362¦
source water 2 | Bacteroides_uniformis | 单形拟杆菌 | 38/5041813 | 0.0008 | 1 | 1 | 1 | Bacteroides | 拟杆菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.03 | 0.0037 | 0.008 | - | - | id¦04686984¦BAC¦R_7973535¦ | id¦25865564¦BAC¦S_4177444¦
source water 2 | Bacteroides_coprocola | 居粪拟杆菌 | 42/4296336 | 0.001 | 1 | 1 | 0 | Bacteroides | 拟杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.03 | 0.0043 | 0.008 | - | - | id¦34788043¦BAC¦R_9751448¦ | id¦92442829¦BAC¦S_9640952¦
source water 2 | Brevilactibacter_sinopodophylli | - | 42/3068364 | 0.0014 | 1 | 1 | 1 | Brevilactibacter | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.006 | 0.006 | - | - | id¦29684576¦BAC¦R_3289712¦ | id¦25545099¦BAC¦S_3723711¦
source water 2 | Caenimonas_koreensis | - | 84/4606362 | 0.0018 | 1 | 2 | 1 | Caenimonas | - | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.03 | 0.008 | 0.008 | - | - | id¦47209943¦BAC¦R_6292553¦ | id¦96725012¦BAC¦S_8573656¦
source water 2 | Campylobacter_concisus | 简明弯曲菌 | 42/1960919 | 0.0021 | 1 | 2 | 1 | Campylobacter | 弯曲菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.06 | 0.06 | 0.0188 | 0.0188 | - | - | id¦11601658¦BAC¦R_8756155¦ | id¦09225893¦BAC¦S_6771200¦
source water 2 | Cellvibrio_mixtus | 混合纤维弧菌 | 123/4773926 | 0.0026 | 1 | 6 | 1 | Cellvibrio | 纤维弧菌属 | 6 | 1 | 2 | 1 | 2 | 1 | G- | 0.08 | 0.08 | 0.0232 | 0.0232 | - | - | id¦57437709¦BAC¦R_9566021¦ | id¦95815400¦BAC¦S_7803496¦
source water 2 | Chakrabartia_godavariana | - | 42/3168868 | 0.0013 | 1 | 1 | 1 | Chakrabartia | - | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.02 | 0.0058 | 0.0058 | - | - | id¦98147693¦BAC¦R_7491570¦ | id¦82021382¦BAC¦S_1257151¦
source water 2 | Chelatococcus_asaccharovorans | 不噬糖螯合球菌 | 42/7254742 | 0.0006 | 1 | 1 | 1 | Chelatococcus | 螯合球菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.02 | 0.0025 | 0.0069 | - | - | id¦37001757¦BAC¦R_4669271¦ | id¦29006020¦BAC¦S_0604929¦
source water 2 | Chelatococcus_daeguensis | 大邱螯合球菌 | 42/4213788 | 0.001 | 1 | 1 | 0 | Chelatococcus | 螯合球菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.02 | 0.0044 | 0.0069 | - | - | id¦04883037¦BAC¦R_8404540¦ | id¦27683155¦BAC¦S_8920707¦
source water 2 | Cnuella_takakiae | - | 42/5659689 | 0.0007 | 1 | 1 | 1 | Cnuella | - | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.01 | 0.0033 | 0.0033 | - | - | id¦13458523¦BAC¦R_3224560¦ | id¦92554377¦BAC¦S_6629791¦
source water 2 | Conchiformibius_steedae | - | 42/2099460 | 0.002 | 1 | 1 | 0 | Conchiformibius | - | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.03 | 0.03 | 0.0088 | 0.0088 | - | - | id¦89772683¦BAC¦R_4328141¦ | id¦15475303¦BAC¦S_1192213¦
source water 2 | Desulfocarbo_indianensis | 印第安纳脱硫煤菌 | 42/4913179 | 0.0009 | 1 | 1 | 1 | Desulfocarbo | 脱硫煤菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.01 | 0.0038 | 0.0038 | - | - | id¦76489373¦BAC¦R_4513793¦ | id¦67688727¦BAC¦S_5687493¦
source water 2 | Desulfohalotomaculum_alkaliphilum | 嗜碱脱硫需盐肠状菌 | 40/2621259 | 0.0015 | 1 | 1 | 1 | Desulfohalotomaculum | 脱硫需盐肠状菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.007 | 0.007 | - | - | id¦53077356¦BAC¦R_9089846¦ | id¦85362881¦BAC¦S_3811167¦
source water 2 | Desulfotomaculum_ferrireducens | 铁还原脱硫肠状菌 | 42/3240180 | 0.0013 | 1 | 1 | 0 | Desulfotomaculum | 脱硫肠状菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0057 | 0.0057 | - | - | id¦74462681¦BAC¦R_4428675¦ | id¦97532195¦BAC¦S_6764262¦
source water 2 | Domibacillus_enclensis | - | 42/3835960 | 0.0011 | 1 | 1 | 1 | Domibacillus | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0048 | 0.0048 | - | - | id¦30542898¦BAC¦R_0619356¦ | id¦17475482¦BAC¦S_2166475¦
source water 2 | Dorea_longicatena | 长链多尔菌 | 42/3322908 | 0.0013 | 1 | 1 | 1 | Dorea | 多尔菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0056 | 0.0056 | - | - | id¦95005892¦BAC¦R_8563185¦ | id¦16112805¦BAC¦S_9906468¦
source water 2 | Elizabethkingia_anophelis | 按蚊伊丽莎白菌 | 42/4360210 | 0.001 | 1 | 2 | 1 | Elizabethkingia | 伊丽莎白菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.03 | 0.0085 | 0.0085 | - | - | id¦27441601¦BAC¦R_4361642¦ | id¦55885875¦BAC¦S_1481425¦
source water 2 | Enhydrobacter_aerosaccus | 气囊栖水菌 | 126/6767419 | 0.0019 | 1 | 3 | 1 | Enhydrobacter | 栖水菌属 | 3 | 1 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.03 | 0.0082 | 0.0082 | - | - | id¦19544319¦BAC¦R_9865596¦ | id¦15638415¦BAC¦S_7626718¦
source water 2 | Escherichia_coli | 大肠埃希菌 | 504/5244439 | 0.0096 | 1 | 15 | 0 | Escherichia | 埃希菌属 | 17 | 1 | 6 | 0 | 6 | 1 | G- | 0.18 | 0.21 | 0.0528 | 0.0605 | 1 | 1 | id¦43058637¦BAC¦R_6156383¦ | id¦80633099¦BAC¦S_9077810¦
source water 2 | Escherichia_fergusonii | 弗格森埃希菌 | 42/4764038 | 0.0009 | 1 | 1 | 0 | Escherichia | 埃希菌属 | 17 | 1 | 1 | 0 | 6 | 1 | G- | 0.01 | 0.21 | 0.0039 | 0.0605 | - | - | id¦89420842¦BAC¦R_1143482¦ | id¦89649513¦BAC¦S_3570842¦
source water 2 | Ethanoligenens_harbinense | 哈尔滨产乙醇杆菌 | 42/3100123 | 0.0014 | 1 | 1 | 1 | Ethanoligenens | 产乙醇杆菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.006 | 0.006 | - | - | id¦49252975¦BAC¦R_8150880¦ | id¦80456744¦BAC¦S_4015428¦
source water 2 | Eubacterium_aggregans | 聚集真杆菌 | 42/2834121 | 0.0015 | 1 | 1 | 1 | Eubacterium | 真杆菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.04 | 0.0065 | 0.0108 | - | - | id¦26172642¦BAC¦R_0800404¦ | id¦57585539¦BAC¦S_3990120¦
source water 2 | Eubacterium_callanderi | 卡氏真杆菌 | 42/4316707 | 0.001 | 1 | 1 | 0 | Eubacterium | 真杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G+ | 0.01 | 0.04 | 0.0043 | 0.0108 | - | - | id¦13626674¦BAC¦R_2090453¦ | id¦85668841¦BAC¦S_9476342¦
source water 2 | Faecalicatena_contorta | - | 42/4707961 | 0.0009 | 1 | 1 | 1 | Faecalicatena | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.01 | 0.01 | 0.0039 | 0.0039 | - | - | id¦21431245¦BAC¦R_6336748¦ | id¦22239479¦BAC¦S_7701008¦
source water 2 | Finegoldia_magna | 大芬戈尔德菌 | 42/1827781 | 0.0023 | 1 | 1 | 1 | Finegoldia | 芬戈尔德菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.03 | 0.03 | 0.0101 | 0.0101 | - | - | id¦31014960¦BAC¦R_3821949¦ | id¦96027472¦BAC¦S_9699449¦
source water 2 | Flavimobilis_marinus | - | 42/2899850 | 0.0014 | 1 | 1 | 1 | Flavimobilis | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0064 | 0.0064 | - | - | id¦28751300¦BAC¦R_2918102¦ | id¦63672364¦BAC¦S_2290212¦
source water 2 | Fonticella_tunisiensis | - | 42/3103577 | 0.0014 | 1 | 1 | 1 | Fonticella | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0059 | 0.0059 | - | - | id¦24576637¦BAC¦R_7803428¦ | id¦61290048¦BAC¦S_4986606¦
source water 2 | Frankia_alni | 棺木弗兰克菌 | 38/7497934 | 0.0005 | 1.97 | 2 | 1 | Frankia | 弗兰克菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0049 | 0.0049 | - | - | id¦42681374¦BAC¦R_8060550¦ | id¦96926503¦BAC¦S_7136790¦
source water 2 | Friedmanniella_flava | 黄色弗莱德门菌 | 39/4788213 | 0.0008 | 1 | 1 | 1 | Friedmanniella | 弗莱德门菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G+ | 0.01 | 0.03 | 0.0039 | 0.0078 | - | - | id¦04325647¦BAC¦R_2172392¦ | id¦39208677¦BAC¦S_1744080¦
source water 2 | Friedmanniella_luteola | 黄色弗莱德门菌 | 42/4717524 | 0.0009 | 1 | 1 | 0 | Friedmanniella | 弗莱德门菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G+ | 0.01 | 0.03 | 0.0039 | 0.0078 | - | - | id¦45059419¦BAC¦R_8189599¦ | id¦91995220¦BAC¦S_3607892¦
source water 2 | Glutamicibacter_mysorens | 迈索尔谷氨酸杆菌 | 42/3459735 | 0.0012 | 1 | 1 | 0 | Glutamicibacter | 谷氨酸杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G+ | 0.02 | 0.03 | 0.0053 | 0.0101 | - | - | id¦72484000¦BAC¦R_1036720¦ | id¦12858287¦BAC¦S_9054788¦
source water 2 | Glutamicibacter_soli | 土壤谷氨酸杆菌 | 42/3838795 | 0.0011 | 1 | 1 | 0 | Glutamicibacter | 谷氨酸杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G+ | 0.02 | 0.03 | 0.0048 | 0.0101 | - | - | id¦72353755¦BAC¦R_7360396¦ | id¦34596539¦BAC¦S_7041848¦
source water 2 | Gulosibacter_chungangensis | - | 42/3237382 | 0.0013 | 1 | 1 | 1 | Gulosibacter | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0057 | 0.0057 | - | - | id¦69086947¦BAC¦R_7982697¦ | id¦71639642¦BAC¦S_9085252¦
source water 2 | Helicobacter_pylori | 幽门螺杆菌 | 42/1600345 | 0.0026 | 1 | 1 | 1 | Helicobacter | 螺杆菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.04 | 0.04 | 0.0115 | 0.0115 | - | - | id¦39764119¦BAC¦R_6895672¦ | id¦07466681¦BAC¦S_3371603¦
source water 2 | Hephaestia_caeni | - | 84/4524787 | 0.0019 | 1 | 2 | 1 | Hephaestia | - | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.03 | 0.0082 | 0.0082 | - | - | id¦72003631¦BAC¦R_6248753¦ | id¦19766694¦BAC¦S_2153138¦
source water 2 | Hydrotalea_sandarakina | - | 168/3262857 | 0.0051 | 1 | 4 | 1 | Hydrotalea | - | 5 | 1 | 1 | 1 | 2 | 1 | G- | 0.08 | 0.14 | 0.0226 | 0.0393 | 1 | 0.51 | id¦67914098¦BAC¦R_4600360¦ | id¦08121401¦BAC¦S_7500808¦
source water 2 | Hydrotalea_flava | - | 42/1107739 | 0.0038 | 1 | 1 | 0 | Hydrotalea | - | 5 | 1 | 1 | 0 | 2 | 1 | G- | 0.06 | 0.14 | 0.0167 | 0.0393 | - | - | id¦20797546¦BAC¦R_4878868¦ | id¦94051955¦BAC¦S_8621411¦
source water 2 | Hymenobacter_jeollabukensis | 全罗北道薄层菌 | 42/6177237 | 0.0007 | 1 | 1 | 1 | Hymenobacter | 薄层菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.02 | 0.003 | 0.007 | - | - | id¦93396300¦BAC¦R_4763256¦ | id¦65602632¦BAC¦S_7689070¦
source water 2 | Hymenobacter_lapidarius | 石头薄层菌 | 40/4639448 | 0.0009 | 1 | 1 | 0 | Hymenobacter | 薄层菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.02 | 0.004 | 0.007 | - | - | id¦54771321¦BAC¦R_8115491¦ | id¦16747628¦BAC¦S_2777985¦
source water 2 | Hyphomicrobium_facile | 敏捷生丝微菌 | 84/4425394 | 0.0019 | 1 | 2 | 1 | Hyphomicrobium | 生丝微菌属 | 3 | 1 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.05 | 0.0083 | 0.0134 | - | - | id¦20135672¦BAC¦R_9926749¦ | id¦64547944¦BAC¦S_1894229¦
source water 2 | Hyphomicrobium_nitrativorans | 食硝酸盐生丝微菌 | 42/3653837 | 0.0011 | 1 | 1 | 0 | Hyphomicrobium | 生丝微菌属 | 3 | 1 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.05 | 0.0051 | 0.0134 | - | - | id¦24100748¦BAC¦R_2845784¦ | id¦49753985¦BAC¦S_2937564¦
source water 2 | Kaistia_adipata | - | 38/4836484 | 0.0008 | 1 | 1 | 0 | Kaistia | - | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.03 | 0.0038 | 0.0077 | - | - | id¦22309261¦BAC¦R_4669519¦ | id¦94092489¦BAC¦S_0589491¦
source water 2 | Kaistia_granuli | - | 42/4766297 | 0.0009 | 1 | 1 | 0 | Kaistia | - | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.03 | 0.0039 | 0.0077 | - | - | id¦00521577¦BAC¦R_2768267¦ | id¦62930021¦BAC¦S_3945049¦
source water 2 | Komagataeibacter_europaeus | 欧洲驹形杆菌 | 42/3543138 | 0.0012 | 1 | 1 | 1 | Komagataeibacter | 驹形杆菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.04 | 0.0052 | 0.0106 | - | - | id¦34970251¦BAC¦R_6575728¦ | id¦65962984¦BAC¦S_4227554¦
source water 2 | Komagataeibacter_cocois | 椰奶驹形杆菌 | 37/3398600 | 0.0011 | 1 | 1 | 0 | Komagataeibacter | 驹形杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.04 | 0.0054 | 0.0106 | - | - | id¦53475520¦BAC¦R_2444718¦ | id¦15969683¦BAC¦S_4422574¦
source water 2 | Kurthia_gibsonii | 吉氏库特菌 | 42/2776140 | 0.0015 | 1 | 1 | 1 | Kurthia | 库特菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0066 | 0.0066 | - | - | id¦49823918¦BAC¦R_1005076¦ | id¦08286226¦BAC¦S_8760767¦
source water 2 | Lachnoanaerobaculum_saburreum | - | 42/2901910 | 0.0014 | 1 | 1 | 0 | Lachnoanaerobaculum | - | 2 | 1 | 1 | 0 | 1 | 1 | G+ | 0.02 | 0.04 | 0.0064 | 0.013 | - | - | id¦78712898¦BAC¦R_9022791¦ | id¦00903593¦BAC¦S_5213486¦
source water 2 | Lachnoanaerobaculum_umeaense | - | 42/2810441 | 0.0015 | 1 | 1 | 0 | Lachnoanaerobaculum | - | 2 | 1 | 1 | 0 | 1 | 1 | G+ | 0.02 | 0.04 | 0.0066 | 0.013 | - | - | id¦12698730¦BAC¦R_6377195¦ | id¦96749373¦BAC¦S_6370155¦
source water 2 | Lelliottia_amnigena | 河生莱略特菌 | 42/4471442 | 0.0009 | 1 | 1 | 1 | Lelliottia | 莱略特菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.03 | 0.0041 | 0.0079 | - | - | id¦77047342¦BAC¦R_2813021¦ | id¦64668397¦BAC¦S_3103338¦
source water 2 | Lelliottia_aquatilis | 水生莱略特菌 | 42/4799028 | 0.0009 | 1 | 1 | 0 | Lelliottia | 莱略特菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.03 | 0.0038 | 0.0079 | - | - | id¦29474453¦BAC¦R_9965472¦ | id¦26150967¦BAC¦S_6621590¦
source water 2 | Luteibacter_anthropi | 人类藤黄杆菌 | 42/5069487 | 0.0008 | 1 | 1 | 1 | Luteibacter | 藤黄杆菌属 | 3 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.04 | 0.0036 | 0.0112 | - | - | id¦72815617¦BAC¦R_5005597¦ | id¦61138487¦BAC¦S_8093310¦
source water 2 | Luteibacter_rhizovicinus | 近根藤黄杆菌 | 42/4827340 | 0.0009 | 1 | 2 | 0 | Luteibacter | 藤黄杆菌属 | 3 | 1 | 1 | 0 | 1 | 1 | G- | 0.03 | 0.04 | 0.0076 | 0.0112 | - | - | id¦38252498¦BAC¦R_9333445¦ | id¦82829191¦BAC¦S_5925828¦
source water 2 | Lysinibacillus_fusiformis | 纺锤形赖氨酸芽胞杆菌 | 42/4814053 | 0.0009 | 1 | 1 | 0 | Lysinibacillus | 赖氨酸芽胞杆菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G+ | 0.01 | 0.01 | 0.0038 | 0.0038 | - | - | id¦34008597¦BAC¦R_2913955¦ | id¦56947309¦BAC¦S_1287403¦
source water 2 | Marinococcus_halotolerans | 耐盐海球菌 | 42/3140229 | 0.0013 | 1 | 1 | 0 | Marinococcus | 海球菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0059 | 0.0059 | - | - | id¦93192933¦BAC¦R_7826650¦ | id¦48347853¦BAC¦S_7564442¦
source water 2 | Megasphaera_cerevisiae | 啤酒巨球形菌 | 42/3190514 | 0.0013 | 1 | 1 | 1 | Megasphaera | 巨球形菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.02 | 0.0058 | 0.0058 | - | - | id¦53666881¦BAC¦R_1064760¦ | id¦31418261¦BAC¦S_4530390¦
source water 2 | Methylacidimicrobium_tartarophylax | 甲基酸微菌* | 40/2322277 | 0.0017 | 1 | 1 | 0 | Methylacidimicrobium | 甲基酸微菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.03 | 0.03 | 0.0079 | 0.0079 | - | - | id¦80829430¦BAC¦R_1800365¦ | id¦96908051¦BAC¦S_4861054¦
source water 2 | Novosphingobium_barchaimii | 巴尔哈伊姆氏新鞘氨醇杆菌 | 42/5794447 | 0.0007 | 1 | 2 | 0 | Novosphingobium | 新鞘氨醇杆菌属 | 8 | 1 | 1 | 0 | 3 | 1 | G- | 0.02 | 0.11 | 0.0064 | 0.0315 | - | - | id¦49698619¦BAC¦R_7983187¦ | id¦48423869¦BAC¦S_8701741¦
source water 2 | Novosphingobium_fuchskuhlense | 富克斯库赫勒新鞘氨醇杆菌 | 84/3962997 | 0.0021 | 1 | 2 | 0 | Novosphingobium | 新鞘氨醇杆菌属 | 8 | 1 | 1 | 0 | 3 | 1 | G- | 0.03 | 0.11 | 0.0093 | 0.0315 | - | - | id¦04117579¦BAC¦R_7425413¦ | id¦99787110¦BAC¦S_8081111¦
source water 2 | Oligotropha_carboxidovorans | 食羧寡养菌 | 38/3745629 | 0.001 | 1 | 1 | 1 | Oligotropha | 寡养菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.02 | 0.0049 | 0.0049 | - | - | id¦84191222¦BAC¦R_1724087¦ | id¦41630597¦BAC¦S_2394586¦
source water 2 | Paenibacillus_lentimorbus | 缓病类芽胞杆菌 | 42/3908221 | 0.0011 | 1 | 1 | 1 | Paenibacillus | 类芽胞杆菌属 | 2 | 1 | 1 | 1 | 1 | 1 | Gram-variable | 0.02 | 0.03 | 0.0047 | 0.0089 | - | - | id¦61572666¦BAC¦R_2044370¦ | id¦57684713¦BAC¦S_7021555¦
source water 2 | Paenibacillus_bovis | 牛类芽胞杆菌 | 42/4443223 | 0.0009 | 1 | 1 | 0 | Paenibacillus | 类芽胞杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G+ | 0.01 | 0.03 | 0.0042 | 0.0089 | - | - | id¦15875339¦BAC¦R_9798069¦ | id¦28344424¦BAC¦S_0775817¦
source water 2 | Pandoraea_norimbergensis | 纽伦堡潘多拉菌 | 84/6167370 | 0.0014 | 1 | 2 | 1 | Pandoraea | 潘多拉菌属 | 6 | 1 | 1 | 1 | 2 | 1 | G- | 0.02 | 0.06 | 0.006 | 0.0188 | - | - | id¦99625227¦BAC¦R_8770721¦ | id¦76285503¦BAC¦S_6114923¦
source water 2 | Pandoraea_fibrosis | 纤维化潘多拉菌 | 37/5592065 | 0.0007 | 1 | 1 | 0 | Pandoraea | 潘多拉菌属 | 6 | 1 | 1 | 0 | 2 | 1 | G- | 0.01 | 0.06 | 0.0033 | 0.0188 | - | - | id¦57551003¦BAC¦R_9725517¦ | id¦49890350¦BAC¦S_8238741¦
source water 2 | Pannonibacter_carbonis | - | 42/4780348 | 0.0009 | 1 | 1 | 1 | Pannonibacter | - | 5 | 1 | 1 | 1 | 2 | 1 | G- | 0.01 | 0.06 | 0.0039 | 0.0178 | - | - | id¦95474617¦BAC¦R_1600394¦ | id¦42257716¦BAC¦S_3987934¦
source water 2 | Pannonibacter_phragmitetus | - | 124/5318696 | 0.0023 | 1 | 4 | 0 | Pannonibacter | - | 5 | 1 | 1 | 0 | 2 | 1 | G- | 0.05 | 0.06 | 0.0139 | 0.0178 | - | - | id¦00438562¦BAC¦R_4948719¦ | id¦20344517¦BAC¦S_5365274¦
source water 2 | Peptostreptococcus_anaerobius | 厌氧消化链球菌 | 42/2076696 | 0.002 | 1 | 1 | 1 | Peptostreptococcus | 消化链球菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.03 | 0.03 | 0.0089 | 0.0089 | - | - | id¦53703212¦BAC¦R_7654230¦ | id¦84977996¦BAC¦S_1940768¦
source water 2 | Phenylobacterium_deserti | 沙漠苯基杆菌 | 42/3876629 | 0.0011 | 1 | 1 | 0 | Phenylobacterium | 苯基杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.03 | 0.0048 | 0.0094 | - | - | id¦35289791¦BAC¦R_3583964¦ | id¦55656726¦BAC¦S_0767014¦
source water 2 | Phenylobacterium_zucineum | 苯基杆菌* | 42/3996255 | 0.0011 | 1 | 1 | 0 | Phenylobacterium | 苯基杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.03 | 0.0046 | 0.0094 | - | - | id¦84962002¦BAC¦R_5218018¦ | id¦20546353¦BAC¦S_2950053¦
source water 2 | Phyllobacterium_salinisoli | 盐渍土叶杆菌 | 42/5017535 | 0.0008 | 1 | 1 | 1 | Phyllobacterium | 叶杆菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.01 | 0.0037 | 0.0037 | - | - | id¦73973292¦BAC¦R_9547882¦ | id¦54546893¦BAC¦S_1850425¦
source water 2 | Propionibacterium_freudenreichii | 费氏丙酸杆菌 | 42/2702167 | 0.0016 | 1 | 1 | 1 | Propionibacterium | 丙酸杆菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0068 | 0.0068 | - | - | id¦75709499¦BAC¦R_0114803¦ | id¦19369436¦BAC¦S_4898904¦
source water 2 | Pseudochrobactrum_asaccharolyticum | 不解糖假苍白杆菌 | 42/4649450 | 0.0009 | 1 | 1 | 1 | Pseudochrobactrum | 假苍白杆菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.03 | 0.004 | 0.0089 | - | - | id¦60973006¦BAC¦R_3874517¦ | id¦81121464¦BAC¦S_2432572¦
source water 2 | Pseudochrobactrum_saccharolyticum | 解糖假苍白杆菌 | 42/3762517 | 0.0011 | 1 | 1 | 0 | Pseudochrobactrum | 假苍白杆菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.03 | 0.0049 | 0.0089 | - | - | id¦04771382¦BAC¦R_4593797¦ | id¦77114490¦BAC¦S_0512234¦
source water 2 | Ramlibacter_tataouinensis | - | 84/4070193 | 0.0021 | 1 | 2 | 1 | Ramlibacter | - | 3 | 1 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.05 | 0.0091 | 0.0131 | - | - | id¦64735715¦BAC¦R_0137529¦ | id¦49743193¦BAC¦S_9785338¦
source water 2 | Ramlibacter_rhizophilus | - | 42/4590629 | 0.0009 | 1 | 1 | 0 | Ramlibacter | - | 3 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.05 | 0.004 | 0.0131 | - | - | id¦13275915¦BAC¦R_7401325¦ | id¦87726612¦BAC¦S_9805794¦
source water 2 | Raoultella_ornithinolytica | 解鸟氨酸拉乌尔菌 | 84/5725169 | 0.0015 | 1 | 2 | 0 | Raoultella | 拉乌尔菌属 | 3 | 1 | 1 | 0 | 1 | 1 | G- | 0.02 | 0.03 | 0.0064 | 0.0096 | - | - | id¦22906070¦BAC¦R_4818573¦ | id¦50066746¦BAC¦S_3944516¦
source water 2 | Raoultella_terrigena | 土生拉乌尔菌 | 42/5712623 | 0.0007 | 1 | 1 | 0 | Raoultella | 拉乌尔菌属 | 3 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.03 | 0.0032 | 0.0096 | - | - | id¦73856763¦BAC¦R_6316904¦ | id¦93721172¦BAC¦S_7689395¦
source water 2 | Rheinheimera_nanhaiensis | 南海莱茵海默菌 | 38/3984903 | 0.001 | 1 | 1 | 1 | Rheinheimera | 莱茵海默菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.02 | 0.0046 | 0.0046 | - | - | id¦71857449¦BAC¦R_2578941¦ | id¦96717090¦BAC¦S_3009377¦
source water 2 | Rhizorhabdus_dicambivorans | - | 42/5026772 | 0.0008 | 1 | 1 | 1 | Rhizorhabdus | - | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.01 | 0.0037 | 0.0037 | - | - | id¦23182345¦BAC¦R_3319167¦ | id¦43983512¦BAC¦S_5921855¦
source water 2 | Rhodothermus_marinus | 海洋红嗜热菌 | 42/3261604 | 0.0013 | 1 | 1 | 1 | Rhodothermus | 红嗜热菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.02 | 0.0057 | 0.0057 | - | - | id¦37208861¦BAC¦R_2665942¦ | id¦13896203¦BAC¦S_0156753¦
source water 2 | Rhodovulum_bhavnagarense | 巴夫那加尔小红卵菌 | 124/3156358 | 0.0039 | 1 | 3 | 0 | Rhodovulum | 小红卵菌属 | 10 | 1 | 1 | 0 | 4 | 1 | G- | 0.06 | 0.18 | 0.0175 | 0.0535 | - | - | id¦04990155¦BAC¦R_2814329¦ | id¦41324552¦BAC¦S_4799004¦
source water 2 | Rhodovulum_imhoffii | 英氏小红卵菌 | 84/2909368 | 0.0029 | 1 | 2 | 0 | Rhodovulum | 小红卵菌属 | 10 | 1 | 1 | 0 | 4 | 1 | G- | 0.04 | 0.18 | 0.0127 | 0.0535 | - | - | id¦65443916¦BAC¦R_9769519¦ | id¦40894113¦BAC¦S_8132965¦
source water 2 | Rickettsia_felis | 猫立克次体 | 42/1485148 | 0.0028 | 1 | 1 | 0 | Rickettsia | 立克次体属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.04 | 0.04 | 0.0124 | 0.0124 | - | - | id¦07204482¦BAC¦R_8455310¦ | id¦00944831¦BAC¦S_6004048¦
source water 2 | Roseivivax_sediminis | - | 78/4624543 | 0.0017 | 1.45 | 3 | 1 | Roseivivax | - | 8 | 1 | 1 | 1 | 3 | 1 | G- | 0.04 | 0.11 | 0.012 | 0.0323 | - | - | id¦32944862¦BAC¦R_9825648¦ | id¦14720944¦BAC¦S_1004442¦
source water 2 | Roseivivax_halotolerans | - | 42/3771569 | 0.0011 | 1 | 1 | 0 | Roseivivax | - | 8 | 1 | 1 | 0 | 3 | 1 | G- | 0.02 | 0.11 | 0.0049 | 0.0323 | - | - | id¦19989317¦BAC¦R_9289532¦ | id¦77146431¦BAC¦S_4062616¦
source water 2 | Roseovarius_azorensis | 亚速尔群岛玫瑰变色菌 | 42/3857533 | 0.0011 | 1 | 1 | 1 | Roseovarius | 玫瑰变色菌属 | 12 | 1 | 1 | 1 | 4 | 1 | G- | 0.02 | 0.18 | 0.0048 | 0.0533 | - | - | id¦62294070¦BAC¦R_2597588¦ | id¦10419969¦BAC¦S_6556879¦
source water 2 | Roseovarius_atlanticus | 大西洋玫瑰变色菌 | 84/4568365 | 0.0018 | 1 | 2 | 0 | Roseovarius | 玫瑰变色菌属 | 12 | 1 | 1 | 0 | 4 | 1 | G- | 0.03 | 0.18 | 0.0081 | 0.0533 | - | - | id¦94154551¦BAC¦R_2683094¦ | id¦06393238¦BAC¦S_0391985¦
source water 2 | Rudaeicoccus_suwonensis | - | 42/3827895 | 0.0011 | 1 | 1 | 1 | Rudaeicoccus | - | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0048 | 0.0048 | - | - | id¦81822517¦BAC¦R_8064111¦ | id¦36694779¦BAC¦S_9936298¦
source water 2 | Salegentibacter_agarivorans | 食琼脂需盐杆菌 | 42/4298706 | 0.001 | 1 | 1 | 0 | Salegentibacter | 需盐杆菌属 | 1 | 1 | 1 | 0 | 1 | 1 | G- | 0.01 | 0.01 | 0.0043 | 0.0043 | - | - | id¦27587357¦BAC¦R_0209194¦ | id¦21471445¦BAC¦S_3914441¦
source water 2 | Salinicoccus_qingdaonensis | 青岛盐水球菌 | 42/2633830 | 0.0016 | 1 | 1 | 1 | Salinicoccus | 盐水球菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.007 | 0.007 | - | - | id¦48608884¦BAC¦R_6327375¦ | id¦08198160¦BAC¦S_0835893¦
source water 2 | Scardovia_wiggsiae | 维格斯氏斯卡多维菌 | 42/1552236 | 0.0027 | 1 | 1 | 1 | Scardovia | 斯卡多维菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.04 | 0.04 | 0.0119 | 0.0119 | - | - | id¦60744494¦BAC¦R_4609844¦ | id¦11086196¦BAC¦S_1989907¦
source water 2 | Serinicoccus_profundi | 深海丝氨酸球菌 | 42/3475711 | 0.0012 | 1 | 1 | 1 | Serinicoccus | 丝氨酸球菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.02 | 0.02 | 0.0053 | 0.0053 | - | - | id¦43464208¦BAC¦R_0602118¦ | id¦07067620¦BAC¦S_2017242¦
source water 2 | Sphingosinicella_ginsenosidimutans | 人参苷转化鞘氨醇胞菌 | 42/3041989 | 0.0014 | 1 | 1 | 1 | Sphingosinicella | 鞘氨醇胞菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.05 | 0.0061 | 0.0135 | - | - | id¦61287769¦BAC¦R_8959253¦ | id¦05998230¦BAC¦S_0639165¦
source water 2 | Sphingosinicella_vermicomposti | 蚯蚓堆肥鞘氨醇胞菌 | 35/2507467 | 0.0014 | 1 | 1 | 0 | Sphingosinicella | 鞘氨醇胞菌属 | 2 | 1 | 1 | 0 | 1 | 1 | G- | 0.03 | 0.05 | 0.0074 | 0.0135 | - | - | id¦43056599¦BAC¦R_5953997¦ | id¦26152739¦BAC¦S_8906560¦
source water 2 | Sporocytophaga_myxococcoides | 黏球生孢噬胞菌 | 42/6341290 | 0.0007 | 1 | 2 | 1 | Sporocytophaga | 生孢噬胞菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.02 | 0.0058 | 0.0058 | - | - | id¦35931376¦BAC¦R_6356035¦ | id¦37070955¦BAC¦S_4793200¦
source water 2 | Tannerella_forsythia | 福赛斯坦纳菌 | 42/3405521 | 0.0012 | 1 | 1 | 1 | Tannerella | 坦纳菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.02 | 0.02 | 0.0054 | 0.0054 | - | - | id¦69700064¦BAC¦R_0104713¦ | id¦17537020¦BAC¦S_3544120¦
source water 2 | Treponema_vincentii | 文氏密螺旋体 | 42/2503794 | 0.0017 | 1 | 1 | 1 | Treponema | 密螺旋体属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.03 | 0.0074 | 0.0074 | - | - | id¦65189792¦BAC¦R_7930988¦ | id¦26917300¦BAC¦S_8972083¦
source water 2 | Variovorax_boronicumulans | 聚硼贪噬菌 | 42/6774635 | 0.0006 | 1 | 1 | 0 | Variovorax | 贪噬菌属 | 7 | 1 | 1 | 0 | 3 | 1 | G- | 0.01 | 0.06 | 0.0027 | 0.0181 | - | - | id¦28321460¦BAC¦R_7167526¦ | id¦00754156¦BAC¦S_5495291¦
source water 2 | Variovorax_gossypii | 棉花贪噬菌 | 42/6301068 | 0.0007 | 1 | 1 | 0 | Variovorax | 贪噬菌属 | 7 | 1 | 1 | 0 | 3 | 1 | G- | 0.01 | 0.06 | 0.0029 | 0.0181 | - | - | id¦28845877¦BAC¦R_6610635¦ | id¦36790568¦BAC¦S_5844584¦
source water 2 | Weissella_confusa | 混淆魏斯菌 | 42/2272911 | 0.0018 | 1 | 1 | 1 | Weissella | 魏斯菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G+ | 0.03 | 0.03 | 0.0081 | 0.0081 | - | - | id¦13792908¦BAC¦R_9172033¦ | id¦05050526¦BAC¦S_4884511¦
source water 2 | Yersinia_massiliensis | 马赛耶尔森菌 | 42/5025065 | 0.0008 | 1 | 1 | 1 | Yersinia | 耶尔森菌属 | 1 | 1 | 1 | 1 | 1 | 1 | G- | 0.01 | 0.01 | 0.0037 | 0.0037 | - | - | id¦58891378¦BAC¦R_4109442¦ | id¦63175895¦BAC¦S_1676800¦
source water 2 | Zoogloea_ramigera | 生枝动胶菌 | 84/4586012 | 0.0018 | 1 | 2 | 1 | Zoogloea | 动胶菌属 | 2 | 1 | 1 | 1 | 1 | 1 | G- | 0.03 | 0.03 | 0.008 | 0.008 | - | - | id¦33319154¦BAC¦R_5471669¦ | id¦51571772¦BAC¦S_0319804¦
source water 2 | Comamonadaceae_bacterium | - | 120/4292425 | 0.0028 | 1 | 8 | 2 | - | - | - | - | 3 | 1 | - | - | - | 0.12 | - | 0.0344 | - | - | - | id¦60002764¦BAC¦R_4592808¦ | id¦72203630¦BAC¦S_5405410¦
source water 2 | [Eubacterium]_rectale | 短真杆菌 | 42/3345582 | 0.0013 | 1 | 1 | 1 | - | - | - | - | 1 | 1 | - | - | G+ | 0.02 | - | 0.0055 | - | - | - | id¦03676049¦BAC¦R_5770891¦ | id¦41670855¦BAC¦S_5007061¦
source water 2 | [Eubacterium]_sulci | 龈沟真杆菌 | 42/1739380 | 0.0024 | 1 | 1 | 1 | - | - | - | - | 1 | 1 | - | - | G+ | 0.04 | - | 0.0106 | - | - | - | id¦39341315¦BAC¦R_5538451¦ | id¦83345205¦BAC¦S_5240668¦
source water 2 | Plectus_murrayi | - | 165/190945241 | 0.0001 | 1 | 4 | 3 | Plectus | - | 4 | 3 | 1 | 1 | 1 | 1 | 17.39 | 17.39 | 0.0004 | 0.0004 | 1 | 0 | id¦11700570¦PARA¦R_9095901¦ | id¦77491993¦PARA¦S_9324283¦
source water 2 | Diplonema_papillatum | - | 84/108309612 | 0.0001 | 1 | 2 | 2 | Diplonema | - | 2 | 2 | 1 | 1 | 1 | 1 | 13.04 | 13.04 | 0.0003 | 0.0003 | - | - | id¦65147139¦PARA¦R_1090431¦ | id¦55987667¦PARA¦S_6081456¦
source water 2 | Gyrodactylus_salaris | 三代虫* | 248/67416872 | 0.0004 | 1 | 6 | 2 | Gyrodactylus | 三代虫属 | 6 | 2 | 2 | 1 | 2 | 1 | 69.57 | 69.57 | 0.0016 | 0.0016 | 1 | 0 | id¦10655746¦PARA¦R_7091036¦ | id¦46094270¦PARA¦S_1328003¦